## EDE
# Proposal_Engineering-Data-Exchange - B.I.G.-EU |  |  |  |  | Comments:
PROJECT_NAME | EDE PA-AC-BAC-64-128 |  |  |  | OA = OU address (1..30)
VERSION_OF_REFERENCEFILE | 4 |  |  |  | IA = IU address (1..64)
TIMESTAMP_OF_LAST_CHANGE | 2015-03-12 |  |  |  | Device Obj. Instance is configurable
AUTHOR_OF_LAST_CHANGE | ccruz |  |  |  | * Depending on temperature units configuration of the gateway: ºC/ºF
VERSION_OF_LAYOUT | 2.1 |  |  |  | ** Can be configured as Multistate Input or Analog Input
#mandatory | mandatory | mandatory | mandatory | mandatory | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional
# keyname | device obj.-instance | object-name | object-type | object-instance | description | present-value-default | min-present-value | max-present-value | settable | supports COV | hi-limit | low-limit | state-text-reference | unit-code | vendor-specific-address
Panasonic AC Gateway | 246 | Panasonic AC Gateway | 8 | 246 | Panasonic AC Gateway |  |  |  | N | N
AdaptorLink1_ErrorCode | 246 | AdaptorLink1_ErrorCode | 13/0** | 16 | AdaptorLink1_ErrorCode |  |  |  | N | Y |  |  | 0
AdaptorLink2_ErrorCode | 246 | AdaptorLink2_ErrorCode | 13/0** | 17 | AdaptorLink2_ErrorCode |  |  |  | N | Y |  |  | 0
OnOff_All | 246 | OnOff_All | 4 | 18 | OnOff_All |  |  |  | Y | Y |  |  | 1
Mode_All | 246 | Mode_All | 14 | 19 | Mode_All |  |  |  | Y | Y |  |  | 3
SetPoint_All | 246 | SetPoint_All | 1 | 20 | SetPoint_All |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
FanSpeed_All | 246 | FanSpeed_All | 14 | 21 | FanSpeed_All |  |  |  | Y | Y |  |  | 4
RemoteControl_Lock_All | 246 | RemoteControl_Lock_All | 14 | 22 | RemoteControl_Lock_All |  |  |  | Y | Y |  |  | 6
Occupancy_All | 246 | Occupancy_All | 14 | 23 | Occupancy_All |  |  |  | Y | Y |  |  | 7
Occ_Cool_SetPoint | 246 | Occ_Cool_SetPoint | 2 | 24 | Occ_Cool_SetPoint |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
Occ_Heat_SetPoint | 246 | Occ_Heat_SetPoint | 2 | 25 | Occ_Heat_SetPoint |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
Unocc_Cool_SetPoint | 246 | Unocc_Cool_SetPoint | 2 | 26 | Unocc_Cool_SetPoint |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
Unocc_Heat_SetPoint | 246 | Unocc_Heat_SetPoint | 2 | 27 | Unocc_Heat_SetPoint |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
Occ_ContinuousCheck | 246 | Occ_ContinuousCheck | 4 | 28 | Occ_ContinuousCheck |  |  |  | Y | Y |  |  | 1
Unocc_DeadbandAction | 246 | Unocc_DeadbandAction | 4 | 29 | Unocc_DeadbandAction |  |  |  | Y | Y |  |  | 1
Consumption_Reset | 246 | Consumption_Reset | 4 | 34 | Consumption_Reset |  |  |  | Y | Y |  |  | 1
IU001_IU_Exist | 246 | IU001_IU_Exist | 3 | 256 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU001_OnOff_status | 246 | IU001_OnOff_status | 3 | 257 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU001_OnOff_command | 246 | IU001_OnOff_command | 4 | 258 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU001_Mode_status | 246 | IU001_Mode_status | 13 | 259 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU001_Mode_command | 246 | IU001_Mode_command | 14 | 260 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU001_SetPoint_status | 246 | IU001_SetPoint_status | 0 | 261 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU001_SetPoint_command | 246 | IU001_SetPoint_command | 1 | 262 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU001_Room_Temperature | 246 | IU001_Room_Temperature | 0 | 263 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU001_FanSpeed_status | 246 | IU001_FanSpeed_status | 13 | 264 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU001_FanSpeed_command | 246 | IU001_FanSpeed_command | 14 | 265 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU001_AirDirection_status | 246 | IU001_AirDirection_status | 13 | 266 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU001_AirDirection_command | 246 | IU001_AirDirection_command | 14 | 267 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU001_FilterSign_status | 246 | IU001_FilterSign_status | 3 | 268 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU001_FilterSign_Reset_command | 246 | IU001_FilterSign_Reset_command | 4 | 269 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU001_ErrorCode | 246 | IU001_ErrorCode | 13/0** | 270 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU001_RemoteControl_Lock | 246 | IU001_RemoteControl_Lock | 19 | 271 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU001_Occupancy | 246 | IU001_Occupancy | 19 | 286 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU001_Consumption_Yesterday | 246 | IU001_Consumption_Yesterday | 0 | 287 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU001_Consumption_Today | 246 | IU001_Consumption_Today | 0 | 288 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU001_Consumption_Total | 246 | IU001_Consumption_Total | 0 | 289 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU002_IU_Exist | 246 | IU002_IU_Exist | 3 | 512 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU002_OnOff_status | 246 | IU002_OnOff_status | 3 | 513 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU002_OnOff_command | 246 | IU002_OnOff_command | 4 | 514 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU002_Mode_status | 246 | IU002_Mode_status | 13 | 515 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU002_Mode_command | 246 | IU002_Mode_command | 14 | 516 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU002_SetPoint_status | 246 | IU002_SetPoint_status | 0 | 517 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU002_SetPoint_command | 246 | IU002_SetPoint_command | 1 | 518 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU002_Room_Temperature | 246 | IU002_Room_Temperature | 0 | 519 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU002_FanSpeed_status | 246 | IU002_FanSpeed_status | 13 | 520 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU002_FanSpeed_command | 246 | IU002_FanSpeed_command | 14 | 521 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU002_AirDirection_status | 246 | IU002_AirDirection_status | 13 | 522 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU002_AirDirection_command | 246 | IU002_AirDirection_command | 14 | 523 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU002_FilterSign_status | 246 | IU002_FilterSign_status | 3 | 524 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU002_FilterSign_Reset_command | 246 | IU002_FilterSign_Reset_command | 4 | 525 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU002_ErrorCode | 246 | IU002_ErrorCode | 13/0** | 526 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU002_RemoteControl_Lock | 246 | IU002_RemoteControl_Lock | 19 | 527 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU002_Occupancy | 246 | IU002_Occupancy | 19 | 542 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU002_Consumption_Yesterday | 246 | IU002_Consumption_Yesterday | 0 | 543 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU002_Consumption_Today | 246 | IU002_Consumption_Today | 0 | 544 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU002_Consumption_Total | 246 | IU002_Consumption_Total | 0 | 545 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU003_IU_Exist | 246 | IU003_IU_Exist | 3 | 768 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU003_OnOff_status | 246 | IU003_OnOff_status | 3 | 769 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU003_OnOff_command | 246 | IU003_OnOff_command | 4 | 770 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU003_Mode_status | 246 | IU003_Mode_status | 13 | 771 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU003_Mode_command | 246 | IU003_Mode_command | 14 | 772 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU003_SetPoint_status | 246 | IU003_SetPoint_status | 0 | 773 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU003_SetPoint_command | 246 | IU003_SetPoint_command | 1 | 774 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU003_Room_Temperature | 246 | IU003_Room_Temperature | 0 | 775 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU003_FanSpeed_status | 246 | IU003_FanSpeed_status | 13 | 776 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU003_FanSpeed_command | 246 | IU003_FanSpeed_command | 14 | 777 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU003_AirDirection_status | 246 | IU003_AirDirection_status | 13 | 778 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU003_AirDirection_command | 246 | IU003_AirDirection_command | 14 | 779 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU003_FilterSign_status | 246 | IU003_FilterSign_status | 3 | 780 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU003_FilterSign_Reset_command | 246 | IU003_FilterSign_Reset_command | 4 | 781 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU003_ErrorCode | 246 | IU003_ErrorCode | 13/0** | 782 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU003_RemoteControl_Lock | 246 | IU003_RemoteControl_Lock | 19 | 783 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU003_Occupancy | 246 | IU003_Occupancy | 19 | 798 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU003_Consumption_Yesterday | 246 | IU003_Consumption_Yesterday | 0 | 799 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU003_Consumption_Today | 246 | IU003_Consumption_Today | 0 | 800 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU003_Consumption_Total | 246 | IU003_Consumption_Total | 0 | 801 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU004_IU_Exist | 246 | IU004_IU_Exist | 3 | 1024 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU004_OnOff_status | 246 | IU004_OnOff_status | 3 | 1025 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU004_OnOff_command | 246 | IU004_OnOff_command | 4 | 1026 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU004_Mode_status | 246 | IU004_Mode_status | 13 | 1027 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU004_Mode_command | 246 | IU004_Mode_command | 14 | 1028 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU004_SetPoint_status | 246 | IU004_SetPoint_status | 0 | 1029 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU004_SetPoint_command | 246 | IU004_SetPoint_command | 1 | 1030 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU004_Room_Temperature | 246 | IU004_Room_Temperature | 0 | 1031 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU004_FanSpeed_status | 246 | IU004_FanSpeed_status | 13 | 1032 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU004_FanSpeed_command | 246 | IU004_FanSpeed_command | 14 | 1033 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU004_AirDirection_status | 246 | IU004_AirDirection_status | 13 | 1034 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU004_AirDirection_command | 246 | IU004_AirDirection_command | 14 | 1035 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU004_FilterSign_status | 246 | IU004_FilterSign_status | 3 | 1036 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU004_FilterSign_Reset_command | 246 | IU004_FilterSign_Reset_command | 4 | 1037 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU004_ErrorCode | 246 | IU004_ErrorCode | 13/0** | 1038 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU004_RemoteControl_Lock | 246 | IU004_RemoteControl_Lock | 19 | 1039 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU004_Occupancy | 246 | IU004_Occupancy | 19 | 1054 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU004_Consumption_Yesterday | 246 | IU004_Consumption_Yesterday | 0 | 1055 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU004_Consumption_Today | 246 | IU004_Consumption_Today | 0 | 1056 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU004_Consumption_Total | 246 | IU004_Consumption_Total | 0 | 1057 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU005_IU_Exist | 246 | IU005_IU_Exist | 3 | 1280 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU005_OnOff_status | 246 | IU005_OnOff_status | 3 | 1281 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU005_OnOff_command | 246 | IU005_OnOff_command | 4 | 1282 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU005_Mode_status | 246 | IU005_Mode_status | 13 | 1283 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU005_Mode_command | 246 | IU005_Mode_command | 14 | 1284 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU005_SetPoint_status | 246 | IU005_SetPoint_status | 0 | 1285 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU005_SetPoint_command | 246 | IU005_SetPoint_command | 1 | 1286 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU005_Room_Temperature | 246 | IU005_Room_Temperature | 0 | 1287 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU005_FanSpeed_status | 246 | IU005_FanSpeed_status | 13 | 1288 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU005_FanSpeed_command | 246 | IU005_FanSpeed_command | 14 | 1289 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU005_AirDirection_status | 246 | IU005_AirDirection_status | 13 | 1290 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU005_AirDirection_command | 246 | IU005_AirDirection_command | 14 | 1291 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU005_FilterSign_status | 246 | IU005_FilterSign_status | 3 | 1292 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU005_FilterSign_Reset_command | 246 | IU005_FilterSign_Reset_command | 4 | 1293 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU005_ErrorCode | 246 | IU005_ErrorCode | 13/0** | 1294 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU005_RemoteControl_Lock | 246 | IU005_RemoteControl_Lock | 19 | 1295 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU005_Occupancy | 246 | IU005_Occupancy | 19 | 1310 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU005_Consumption_Yesterday | 246 | IU005_Consumption_Yesterday | 0 | 1311 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU005_Consumption_Today | 246 | IU005_Consumption_Today | 0 | 1312 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU005_Consumption_Total | 246 | IU005_Consumption_Total | 0 | 1313 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU006_IU_Exist | 246 | IU006_IU_Exist | 3 | 1536 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU006_OnOff_status | 246 | IU006_OnOff_status | 3 | 1537 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU006_OnOff_command | 246 | IU006_OnOff_command | 4 | 1538 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU006_Mode_status | 246 | IU006_Mode_status | 13 | 1539 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU006_Mode_command | 246 | IU006_Mode_command | 14 | 1540 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU006_SetPoint_status | 246 | IU006_SetPoint_status | 0 | 1541 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU006_SetPoint_command | 246 | IU006_SetPoint_command | 1 | 1542 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU006_Room_Temperature | 246 | IU006_Room_Temperature | 0 | 1543 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU006_FanSpeed_status | 246 | IU006_FanSpeed_status | 13 | 1544 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU006_FanSpeed_command | 246 | IU006_FanSpeed_command | 14 | 1545 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU006_AirDirection_status | 246 | IU006_AirDirection_status | 13 | 1546 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU006_AirDirection_command | 246 | IU006_AirDirection_command | 14 | 1547 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU006_FilterSign_status | 246 | IU006_FilterSign_status | 3 | 1548 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU006_FilterSign_Reset_command | 246 | IU006_FilterSign_Reset_command | 4 | 1549 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU006_ErrorCode | 246 | IU006_ErrorCode | 13/0** | 1550 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU006_RemoteControl_Lock | 246 | IU006_RemoteControl_Lock | 19 | 1551 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU006_Occupancy | 246 | IU006_Occupancy | 19 | 1566 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU006_Consumption_Yesterday | 246 | IU006_Consumption_Yesterday | 0 | 1567 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU006_Consumption_Today | 246 | IU006_Consumption_Today | 0 | 1568 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU006_Consumption_Total | 246 | IU006_Consumption_Total | 0 | 1569 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU007_IU_Exist | 246 | IU007_IU_Exist | 3 | 1792 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU007_OnOff_status | 246 | IU007_OnOff_status | 3 | 1793 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU007_OnOff_command | 246 | IU007_OnOff_command | 4 | 1794 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU007_Mode_status | 246 | IU007_Mode_status | 13 | 1795 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU007_Mode_command | 246 | IU007_Mode_command | 14 | 1796 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU007_SetPoint_status | 246 | IU007_SetPoint_status | 0 | 1797 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU007_SetPoint_command | 246 | IU007_SetPoint_command | 1 | 1798 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU007_Room_Temperature | 246 | IU007_Room_Temperature | 0 | 1799 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU007_FanSpeed_status | 246 | IU007_FanSpeed_status | 13 | 1800 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU007_FanSpeed_command | 246 | IU007_FanSpeed_command | 14 | 1801 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU007_AirDirection_status | 246 | IU007_AirDirection_status | 13 | 1802 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU007_AirDirection_command | 246 | IU007_AirDirection_command | 14 | 1803 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU007_FilterSign_status | 246 | IU007_FilterSign_status | 3 | 1804 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU007_FilterSign_Reset_command | 246 | IU007_FilterSign_Reset_command | 4 | 1805 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU007_ErrorCode | 246 | IU007_ErrorCode | 13/0** | 1806 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU007_RemoteControl_Lock | 246 | IU007_RemoteControl_Lock | 19 | 1807 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU007_Occupancy | 246 | IU007_Occupancy | 19 | 1822 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU007_Consumption_Yesterday | 246 | IU007_Consumption_Yesterday | 0 | 1823 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU007_Consumption_Today | 246 | IU007_Consumption_Today | 0 | 1824 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU007_Consumption_Total | 246 | IU007_Consumption_Total | 0 | 1825 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU008_IU_Exist | 246 | IU008_IU_Exist | 3 | 2048 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU008_OnOff_status | 246 | IU008_OnOff_status | 3 | 2049 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU008_OnOff_command | 246 | IU008_OnOff_command | 4 | 2050 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU008_Mode_status | 246 | IU008_Mode_status | 13 | 2051 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU008_Mode_command | 246 | IU008_Mode_command | 14 | 2052 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU008_SetPoint_status | 246 | IU008_SetPoint_status | 0 | 2053 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU008_SetPoint_command | 246 | IU008_SetPoint_command | 1 | 2054 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU008_Room_Temperature | 246 | IU008_Room_Temperature | 0 | 2055 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU008_FanSpeed_status | 246 | IU008_FanSpeed_status | 13 | 2056 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU008_FanSpeed_command | 246 | IU008_FanSpeed_command | 14 | 2057 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU008_AirDirection_status | 246 | IU008_AirDirection_status | 13 | 2058 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU008_AirDirection_command | 246 | IU008_AirDirection_command | 14 | 2059 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU008_FilterSign_status | 246 | IU008_FilterSign_status | 3 | 2060 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU008_FilterSign_Reset_command | 246 | IU008_FilterSign_Reset_command | 4 | 2061 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU008_ErrorCode | 246 | IU008_ErrorCode | 13/0** | 2062 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU008_RemoteControl_Lock | 246 | IU008_RemoteControl_Lock | 19 | 2063 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU008_Occupancy | 246 | IU008_Occupancy | 19 | 2078 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU008_Consumption_Yesterday | 246 | IU008_Consumption_Yesterday | 0 | 2079 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU008_Consumption_Today | 246 | IU008_Consumption_Today | 0 | 2080 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU008_Consumption_Total | 246 | IU008_Consumption_Total | 0 | 2081 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU009_IU_Exist | 246 | IU009_IU_Exist | 3 | 2304 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU009_OnOff_status | 246 | IU009_OnOff_status | 3 | 2305 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU009_OnOff_command | 246 | IU009_OnOff_command | 4 | 2306 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU009_Mode_status | 246 | IU009_Mode_status | 13 | 2307 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU009_Mode_command | 246 | IU009_Mode_command | 14 | 2308 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU009_SetPoint_status | 246 | IU009_SetPoint_status | 0 | 2309 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU009_SetPoint_command | 246 | IU009_SetPoint_command | 1 | 2310 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU009_Room_Temperature | 246 | IU009_Room_Temperature | 0 | 2311 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU009_FanSpeed_status | 246 | IU009_FanSpeed_status | 13 | 2312 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU009_FanSpeed_command | 246 | IU009_FanSpeed_command | 14 | 2313 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU009_AirDirection_status | 246 | IU009_AirDirection_status | 13 | 2314 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU009_AirDirection_command | 246 | IU009_AirDirection_command | 14 | 2315 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU009_FilterSign_status | 246 | IU009_FilterSign_status | 3 | 2316 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU009_FilterSign_Reset_command | 246 | IU009_FilterSign_Reset_command | 4 | 2317 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU009_ErrorCode | 246 | IU009_ErrorCode | 13/0** | 2318 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU009_RemoteControl_Lock | 246 | IU009_RemoteControl_Lock | 19 | 2319 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU009_Occupancy | 246 | IU009_Occupancy | 19 | 2334 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU009_Consumption_Yesterday | 246 | IU009_Consumption_Yesterday | 0 | 2335 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU009_Consumption_Today | 246 | IU009_Consumption_Today | 0 | 2336 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU009_Consumption_Total | 246 | IU009_Consumption_Total | 0 | 2337 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU010_IU_Exist | 246 | IU010_IU_Exist | 3 | 2560 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU010_OnOff_status | 246 | IU010_OnOff_status | 3 | 2561 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU010_OnOff_command | 246 | IU010_OnOff_command | 4 | 2562 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU010_Mode_status | 246 | IU010_Mode_status | 13 | 2563 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU010_Mode_command | 246 | IU010_Mode_command | 14 | 2564 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU010_SetPoint_status | 246 | IU010_SetPoint_status | 0 | 2565 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU010_SetPoint_command | 246 | IU010_SetPoint_command | 1 | 2566 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU010_Room_Temperature | 246 | IU010_Room_Temperature | 0 | 2567 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU010_FanSpeed_status | 246 | IU010_FanSpeed_status | 13 | 2568 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU010_FanSpeed_command | 246 | IU010_FanSpeed_command | 14 | 2569 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU010_AirDirection_status | 246 | IU010_AirDirection_status | 13 | 2570 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU010_AirDirection_command | 246 | IU010_AirDirection_command | 14 | 2571 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU010_FilterSign_status | 246 | IU010_FilterSign_status | 3 | 2572 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU010_FilterSign_Reset_command | 246 | IU010_FilterSign_Reset_command | 4 | 2573 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU010_ErrorCode | 246 | IU010_ErrorCode | 13/0** | 2574 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU010_RemoteControl_Lock | 246 | IU010_RemoteControl_Lock | 19 | 2575 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU010_Occupancy | 246 | IU010_Occupancy | 19 | 2590 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU010_Consumption_Yesterday | 246 | IU010_Consumption_Yesterday | 0 | 2591 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU010_Consumption_Today | 246 | IU010_Consumption_Today | 0 | 2592 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU010_Consumption_Total | 246 | IU010_Consumption_Total | 0 | 2593 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU011_IU_Exist | 246 | IU011_IU_Exist | 3 | 2816 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU011_OnOff_status | 246 | IU011_OnOff_status | 3 | 2817 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU011_OnOff_command | 246 | IU011_OnOff_command | 4 | 2818 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU011_Mode_status | 246 | IU011_Mode_status | 13 | 2819 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU011_Mode_command | 246 | IU011_Mode_command | 14 | 2820 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU011_SetPoint_status | 246 | IU011_SetPoint_status | 0 | 2821 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU011_SetPoint_command | 246 | IU011_SetPoint_command | 1 | 2822 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU011_Room_Temperature | 246 | IU011_Room_Temperature | 0 | 2823 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU011_FanSpeed_status | 246 | IU011_FanSpeed_status | 13 | 2824 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU011_FanSpeed_command | 246 | IU011_FanSpeed_command | 14 | 2825 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU011_AirDirection_status | 246 | IU011_AirDirection_status | 13 | 2826 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU011_AirDirection_command | 246 | IU011_AirDirection_command | 14 | 2827 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU011_FilterSign_status | 246 | IU011_FilterSign_status | 3 | 2828 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU011_FilterSign_Reset_command | 246 | IU011_FilterSign_Reset_command | 4 | 2829 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU011_ErrorCode | 246 | IU011_ErrorCode | 13/0** | 2830 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU011_RemoteControl_Lock | 246 | IU011_RemoteControl_Lock | 19 | 2831 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU011_Occupancy | 246 | IU011_Occupancy | 19 | 2846 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU011_Consumption_Yesterday | 246 | IU011_Consumption_Yesterday | 0 | 2847 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU011_Consumption_Today | 246 | IU011_Consumption_Today | 0 | 2848 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU011_Consumption_Total | 246 | IU011_Consumption_Total | 0 | 2849 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU012_IU_Exist | 246 | IU012_IU_Exist | 3 | 3072 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU012_OnOff_status | 246 | IU012_OnOff_status | 3 | 3073 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU012_OnOff_command | 246 | IU012_OnOff_command | 4 | 3074 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU012_Mode_status | 246 | IU012_Mode_status | 13 | 3075 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU012_Mode_command | 246 | IU012_Mode_command | 14 | 3076 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU012_SetPoint_status | 246 | IU012_SetPoint_status | 0 | 3077 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU012_SetPoint_command | 246 | IU012_SetPoint_command | 1 | 3078 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU012_Room_Temperature | 246 | IU012_Room_Temperature | 0 | 3079 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU012_FanSpeed_status | 246 | IU012_FanSpeed_status | 13 | 3080 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU012_FanSpeed_command | 246 | IU012_FanSpeed_command | 14 | 3081 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU012_AirDirection_status | 246 | IU012_AirDirection_status | 13 | 3082 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU012_AirDirection_command | 246 | IU012_AirDirection_command | 14 | 3083 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU012_FilterSign_status | 246 | IU012_FilterSign_status | 3 | 3084 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU012_FilterSign_Reset_command | 246 | IU012_FilterSign_Reset_command | 4 | 3085 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU012_ErrorCode | 246 | IU012_ErrorCode | 13/0** | 3086 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU012_RemoteControl_Lock | 246 | IU012_RemoteControl_Lock | 19 | 3087 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU012_Occupancy | 246 | IU012_Occupancy | 19 | 3102 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU012_Consumption_Yesterday | 246 | IU012_Consumption_Yesterday | 0 | 3103 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU012_Consumption_Today | 246 | IU012_Consumption_Today | 0 | 3104 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU012_Consumption_Total | 246 | IU012_Consumption_Total | 0 | 3105 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU013_IU_Exist | 246 | IU013_IU_Exist | 3 | 3328 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU013_OnOff_status | 246 | IU013_OnOff_status | 3 | 3329 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU013_OnOff_command | 246 | IU013_OnOff_command | 4 | 3330 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU013_Mode_status | 246 | IU013_Mode_status | 13 | 3331 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU013_Mode_command | 246 | IU013_Mode_command | 14 | 3332 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU013_SetPoint_status | 246 | IU013_SetPoint_status | 0 | 3333 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU013_SetPoint_command | 246 | IU013_SetPoint_command | 1 | 3334 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU013_Room_Temperature | 246 | IU013_Room_Temperature | 0 | 3335 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU013_FanSpeed_status | 246 | IU013_FanSpeed_status | 13 | 3336 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU013_FanSpeed_command | 246 | IU013_FanSpeed_command | 14 | 3337 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU013_AirDirection_status | 246 | IU013_AirDirection_status | 13 | 3338 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU013_AirDirection_command | 246 | IU013_AirDirection_command | 14 | 3339 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU013_FilterSign_status | 246 | IU013_FilterSign_status | 3 | 3340 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU013_FilterSign_Reset_command | 246 | IU013_FilterSign_Reset_command | 4 | 3341 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU013_ErrorCode | 246 | IU013_ErrorCode | 13/0** | 3342 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU013_RemoteControl_Lock | 246 | IU013_RemoteControl_Lock | 19 | 3343 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU013_Occupancy | 246 | IU013_Occupancy | 19 | 3358 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU013_Consumption_Yesterday | 246 | IU013_Consumption_Yesterday | 0 | 3359 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU013_Consumption_Today | 246 | IU013_Consumption_Today | 0 | 3360 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU013_Consumption_Total | 246 | IU013_Consumption_Total | 0 | 3361 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU014_IU_Exist | 246 | IU014_IU_Exist | 3 | 3584 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU014_OnOff_status | 246 | IU014_OnOff_status | 3 | 3585 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU014_OnOff_command | 246 | IU014_OnOff_command | 4 | 3586 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU014_Mode_status | 246 | IU014_Mode_status | 13 | 3587 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU014_Mode_command | 246 | IU014_Mode_command | 14 | 3588 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU014_SetPoint_status | 246 | IU014_SetPoint_status | 0 | 3589 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU014_SetPoint_command | 246 | IU014_SetPoint_command | 1 | 3590 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU014_Room_Temperature | 246 | IU014_Room_Temperature | 0 | 3591 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU014_FanSpeed_status | 246 | IU014_FanSpeed_status | 13 | 3592 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU014_FanSpeed_command | 246 | IU014_FanSpeed_command | 14 | 3593 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU014_AirDirection_status | 246 | IU014_AirDirection_status | 13 | 3594 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU014_AirDirection_command | 246 | IU014_AirDirection_command | 14 | 3595 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU014_FilterSign_status | 246 | IU014_FilterSign_status | 3 | 3596 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU014_FilterSign_Reset_command | 246 | IU014_FilterSign_Reset_command | 4 | 3597 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU014_ErrorCode | 246 | IU014_ErrorCode | 13/0** | 3598 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU014_RemoteControl_Lock | 246 | IU014_RemoteControl_Lock | 19 | 3599 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU014_Occupancy | 246 | IU014_Occupancy | 19 | 3614 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU014_Consumption_Yesterday | 246 | IU014_Consumption_Yesterday | 0 | 3615 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU014_Consumption_Today | 246 | IU014_Consumption_Today | 0 | 3616 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU014_Consumption_Total | 246 | IU014_Consumption_Total | 0 | 3617 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU015_IU_Exist | 246 | IU015_IU_Exist | 3 | 3840 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU015_OnOff_status | 246 | IU015_OnOff_status | 3 | 3841 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU015_OnOff_command | 246 | IU015_OnOff_command | 4 | 3842 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU015_Mode_status | 246 | IU015_Mode_status | 13 | 3843 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU015_Mode_command | 246 | IU015_Mode_command | 14 | 3844 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU015_SetPoint_status | 246 | IU015_SetPoint_status | 0 | 3845 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU015_SetPoint_command | 246 | IU015_SetPoint_command | 1 | 3846 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU015_Room_Temperature | 246 | IU015_Room_Temperature | 0 | 3847 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU015_FanSpeed_status | 246 | IU015_FanSpeed_status | 13 | 3848 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU015_FanSpeed_command | 246 | IU015_FanSpeed_command | 14 | 3849 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU015_AirDirection_status | 246 | IU015_AirDirection_status | 13 | 3850 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU015_AirDirection_command | 246 | IU015_AirDirection_command | 14 | 3851 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU015_FilterSign_status | 246 | IU015_FilterSign_status | 3 | 3852 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU015_FilterSign_Reset_command | 246 | IU015_FilterSign_Reset_command | 4 | 3853 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU015_ErrorCode | 246 | IU015_ErrorCode | 13/0** | 3854 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU015_RemoteControl_Lock | 246 | IU015_RemoteControl_Lock | 19 | 3855 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU015_Occupancy | 246 | IU015_Occupancy | 19 | 3870 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU015_Consumption_Yesterday | 246 | IU015_Consumption_Yesterday | 0 | 3871 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU015_Consumption_Today | 246 | IU015_Consumption_Today | 0 | 3872 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU015_Consumption_Total | 246 | IU015_Consumption_Total | 0 | 3873 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU016_IU_Exist | 246 | IU016_IU_Exist | 3 | 4096 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU016_OnOff_status | 246 | IU016_OnOff_status | 3 | 4097 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU016_OnOff_command | 246 | IU016_OnOff_command | 4 | 4098 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU016_Mode_status | 246 | IU016_Mode_status | 13 | 4099 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU016_Mode_command | 246 | IU016_Mode_command | 14 | 4100 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU016_SetPoint_status | 246 | IU016_SetPoint_status | 0 | 4101 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU016_SetPoint_command | 246 | IU016_SetPoint_command | 1 | 4102 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU016_Room_Temperature | 246 | IU016_Room_Temperature | 0 | 4103 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU016_FanSpeed_status | 246 | IU016_FanSpeed_status | 13 | 4104 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU016_FanSpeed_command | 246 | IU016_FanSpeed_command | 14 | 4105 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU016_AirDirection_status | 246 | IU016_AirDirection_status | 13 | 4106 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU016_AirDirection_command | 246 | IU016_AirDirection_command | 14 | 4107 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU016_FilterSign_status | 246 | IU016_FilterSign_status | 3 | 4108 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU016_FilterSign_Reset_command | 246 | IU016_FilterSign_Reset_command | 4 | 4109 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU016_ErrorCode | 246 | IU016_ErrorCode | 13/0** | 4110 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU016_RemoteControl_Lock | 246 | IU016_RemoteControl_Lock | 19 | 4111 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU016_Occupancy | 246 | IU016_Occupancy | 19 | 4126 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU016_Consumption_Yesterday | 246 | IU016_Consumption_Yesterday | 0 | 4127 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU016_Consumption_Today | 246 | IU016_Consumption_Today | 0 | 4128 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU016_Consumption_Total | 246 | IU016_Consumption_Total | 0 | 4129 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU017_IU_Exist | 246 | IU017_IU_Exist | 3 | 4352 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU017_OnOff_status | 246 | IU017_OnOff_status | 3 | 4353 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU017_OnOff_command | 246 | IU017_OnOff_command | 4 | 4354 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU017_Mode_status | 246 | IU017_Mode_status | 13 | 4355 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU017_Mode_command | 246 | IU017_Mode_command | 14 | 4356 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU017_SetPoint_status | 246 | IU017_SetPoint_status | 0 | 4357 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU017_SetPoint_command | 246 | IU017_SetPoint_command | 1 | 4358 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU017_Room_Temperature | 246 | IU017_Room_Temperature | 0 | 4359 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU017_FanSpeed_status | 246 | IU017_FanSpeed_status | 13 | 4360 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU017_FanSpeed_command | 246 | IU017_FanSpeed_command | 14 | 4361 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU017_AirDirection_status | 246 | IU017_AirDirection_status | 13 | 4362 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU017_AirDirection_command | 246 | IU017_AirDirection_command | 14 | 4363 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU017_FilterSign_status | 246 | IU017_FilterSign_status | 3 | 4364 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU017_FilterSign_Reset_command | 246 | IU017_FilterSign_Reset_command | 4 | 4365 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU017_ErrorCode | 246 | IU017_ErrorCode | 13/0** | 4366 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU017_RemoteControl_Lock | 246 | IU017_RemoteControl_Lock | 19 | 4367 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU017_Occupancy | 246 | IU017_Occupancy | 19 | 4382 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU017_Consumption_Yesterday | 246 | IU017_Consumption_Yesterday | 0 | 4383 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU017_Consumption_Today | 246 | IU017_Consumption_Today | 0 | 4384 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU017_Consumption_Total | 246 | IU017_Consumption_Total | 0 | 4385 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU018_IU_Exist | 246 | IU018_IU_Exist | 3 | 4608 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU018_OnOff_status | 246 | IU018_OnOff_status | 3 | 4609 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU018_OnOff_command | 246 | IU018_OnOff_command | 4 | 4610 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU018_Mode_status | 246 | IU018_Mode_status | 13 | 4611 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU018_Mode_command | 246 | IU018_Mode_command | 14 | 4612 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU018_SetPoint_status | 246 | IU018_SetPoint_status | 0 | 4613 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU018_SetPoint_command | 246 | IU018_SetPoint_command | 1 | 4614 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU018_Room_Temperature | 246 | IU018_Room_Temperature | 0 | 4615 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU018_FanSpeed_status | 246 | IU018_FanSpeed_status | 13 | 4616 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU018_FanSpeed_command | 246 | IU018_FanSpeed_command | 14 | 4617 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU018_AirDirection_status | 246 | IU018_AirDirection_status | 13 | 4618 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU018_AirDirection_command | 246 | IU018_AirDirection_command | 14 | 4619 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU018_FilterSign_status | 246 | IU018_FilterSign_status | 3 | 4620 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU018_FilterSign_Reset_command | 246 | IU018_FilterSign_Reset_command | 4 | 4621 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU018_ErrorCode | 246 | IU018_ErrorCode | 13/0** | 4622 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU018_RemoteControl_Lock | 246 | IU018_RemoteControl_Lock | 19 | 4623 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU018_Occupancy | 246 | IU018_Occupancy | 19 | 4638 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU018_Consumption_Yesterday | 246 | IU018_Consumption_Yesterday | 0 | 4639 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU018_Consumption_Today | 246 | IU018_Consumption_Today | 0 | 4640 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU018_Consumption_Total | 246 | IU018_Consumption_Total | 0 | 4641 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU019_IU_Exist | 246 | IU019_IU_Exist | 3 | 4864 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU019_OnOff_status | 246 | IU019_OnOff_status | 3 | 4865 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU019_OnOff_command | 246 | IU019_OnOff_command | 4 | 4866 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU019_Mode_status | 246 | IU019_Mode_status | 13 | 4867 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU019_Mode_command | 246 | IU019_Mode_command | 14 | 4868 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU019_SetPoint_status | 246 | IU019_SetPoint_status | 0 | 4869 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU019_SetPoint_command | 246 | IU019_SetPoint_command | 1 | 4870 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU019_Room_Temperature | 246 | IU019_Room_Temperature | 0 | 4871 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU019_FanSpeed_status | 246 | IU019_FanSpeed_status | 13 | 4872 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU019_FanSpeed_command | 246 | IU019_FanSpeed_command | 14 | 4873 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU019_AirDirection_status | 246 | IU019_AirDirection_status | 13 | 4874 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU019_AirDirection_command | 246 | IU019_AirDirection_command | 14 | 4875 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU019_FilterSign_status | 246 | IU019_FilterSign_status | 3 | 4876 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU019_FilterSign_Reset_command | 246 | IU019_FilterSign_Reset_command | 4 | 4877 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU019_ErrorCode | 246 | IU019_ErrorCode | 13/0** | 4878 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU019_RemoteControl_Lock | 246 | IU019_RemoteControl_Lock | 19 | 4879 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU019_Occupancy | 246 | IU019_Occupancy | 19 | 4894 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU019_Consumption_Yesterday | 246 | IU019_Consumption_Yesterday | 0 | 4895 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU019_Consumption_Today | 246 | IU019_Consumption_Today | 0 | 4896 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU019_Consumption_Total | 246 | IU019_Consumption_Total | 0 | 4897 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU020_IU_Exist | 246 | IU020_IU_Exist | 3 | 5120 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU020_OnOff_status | 246 | IU020_OnOff_status | 3 | 5121 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU020_OnOff_command | 246 | IU020_OnOff_command | 4 | 5122 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU020_Mode_status | 246 | IU020_Mode_status | 13 | 5123 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU020_Mode_command | 246 | IU020_Mode_command | 14 | 5124 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU020_SetPoint_status | 246 | IU020_SetPoint_status | 0 | 5125 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU020_SetPoint_command | 246 | IU020_SetPoint_command | 1 | 5126 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU020_Room_Temperature | 246 | IU020_Room_Temperature | 0 | 5127 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU020_FanSpeed_status | 246 | IU020_FanSpeed_status | 13 | 5128 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU020_FanSpeed_command | 246 | IU020_FanSpeed_command | 14 | 5129 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU020_AirDirection_status | 246 | IU020_AirDirection_status | 13 | 5130 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU020_AirDirection_command | 246 | IU020_AirDirection_command | 14 | 5131 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU020_FilterSign_status | 246 | IU020_FilterSign_status | 3 | 5132 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU020_FilterSign_Reset_command | 246 | IU020_FilterSign_Reset_command | 4 | 5133 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU020_ErrorCode | 246 | IU020_ErrorCode | 13/0** | 5134 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU020_RemoteControl_Lock | 246 | IU020_RemoteControl_Lock | 19 | 5135 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU020_Occupancy | 246 | IU020_Occupancy | 19 | 5150 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU020_Consumption_Yesterday | 246 | IU020_Consumption_Yesterday | 0 | 5151 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU020_Consumption_Today | 246 | IU020_Consumption_Today | 0 | 5152 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU020_Consumption_Total | 246 | IU020_Consumption_Total | 0 | 5153 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU021_IU_Exist | 246 | IU021_IU_Exist | 3 | 5376 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU021_OnOff_status | 246 | IU021_OnOff_status | 3 | 5377 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU021_OnOff_command | 246 | IU021_OnOff_command | 4 | 5378 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU021_Mode_status | 246 | IU021_Mode_status | 13 | 5379 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU021_Mode_command | 246 | IU021_Mode_command | 14 | 5380 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU021_SetPoint_status | 246 | IU021_SetPoint_status | 0 | 5381 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU021_SetPoint_command | 246 | IU021_SetPoint_command | 1 | 5382 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU021_Room_Temperature | 246 | IU021_Room_Temperature | 0 | 5383 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU021_FanSpeed_status | 246 | IU021_FanSpeed_status | 13 | 5384 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU021_FanSpeed_command | 246 | IU021_FanSpeed_command | 14 | 5385 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU021_AirDirection_status | 246 | IU021_AirDirection_status | 13 | 5386 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU021_AirDirection_command | 246 | IU021_AirDirection_command | 14 | 5387 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU021_FilterSign_status | 246 | IU021_FilterSign_status | 3 | 5388 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU021_FilterSign_Reset_command | 246 | IU021_FilterSign_Reset_command | 4 | 5389 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU021_ErrorCode | 246 | IU021_ErrorCode | 13/0** | 5390 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU021_RemoteControl_Lock | 246 | IU021_RemoteControl_Lock | 19 | 5391 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU021_Occupancy | 246 | IU021_Occupancy | 19 | 5406 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU021_Consumption_Yesterday | 246 | IU021_Consumption_Yesterday | 0 | 5407 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU021_Consumption_Today | 246 | IU021_Consumption_Today | 0 | 5408 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU021_Consumption_Total | 246 | IU021_Consumption_Total | 0 | 5409 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU022_IU_Exist | 246 | IU022_IU_Exist | 3 | 5632 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU022_OnOff_status | 246 | IU022_OnOff_status | 3 | 5633 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU022_OnOff_command | 246 | IU022_OnOff_command | 4 | 5634 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU022_Mode_status | 246 | IU022_Mode_status | 13 | 5635 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU022_Mode_command | 246 | IU022_Mode_command | 14 | 5636 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU022_SetPoint_status | 246 | IU022_SetPoint_status | 0 | 5637 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU022_SetPoint_command | 246 | IU022_SetPoint_command | 1 | 5638 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU022_Room_Temperature | 246 | IU022_Room_Temperature | 0 | 5639 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU022_FanSpeed_status | 246 | IU022_FanSpeed_status | 13 | 5640 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU022_FanSpeed_command | 246 | IU022_FanSpeed_command | 14 | 5641 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU022_AirDirection_status | 246 | IU022_AirDirection_status | 13 | 5642 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU022_AirDirection_command | 246 | IU022_AirDirection_command | 14 | 5643 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU022_FilterSign_status | 246 | IU022_FilterSign_status | 3 | 5644 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU022_FilterSign_Reset_command | 246 | IU022_FilterSign_Reset_command | 4 | 5645 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU022_ErrorCode | 246 | IU022_ErrorCode | 13/0** | 5646 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU022_RemoteControl_Lock | 246 | IU022_RemoteControl_Lock | 19 | 5647 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU022_Occupancy | 246 | IU022_Occupancy | 19 | 5662 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU022_Consumption_Yesterday | 246 | IU022_Consumption_Yesterday | 0 | 5663 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU022_Consumption_Today | 246 | IU022_Consumption_Today | 0 | 5664 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU022_Consumption_Total | 246 | IU022_Consumption_Total | 0 | 5665 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU023_IU_Exist | 246 | IU023_IU_Exist | 3 | 5888 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU023_OnOff_status | 246 | IU023_OnOff_status | 3 | 5889 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU023_OnOff_command | 246 | IU023_OnOff_command | 4 | 5890 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU023_Mode_status | 246 | IU023_Mode_status | 13 | 5891 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU023_Mode_command | 246 | IU023_Mode_command | 14 | 5892 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU023_SetPoint_status | 246 | IU023_SetPoint_status | 0 | 5893 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU023_SetPoint_command | 246 | IU023_SetPoint_command | 1 | 5894 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU023_Room_Temperature | 246 | IU023_Room_Temperature | 0 | 5895 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU023_FanSpeed_status | 246 | IU023_FanSpeed_status | 13 | 5896 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU023_FanSpeed_command | 246 | IU023_FanSpeed_command | 14 | 5897 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU023_AirDirection_status | 246 | IU023_AirDirection_status | 13 | 5898 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU023_AirDirection_command | 246 | IU023_AirDirection_command | 14 | 5899 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU023_FilterSign_status | 246 | IU023_FilterSign_status | 3 | 5900 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU023_FilterSign_Reset_command | 246 | IU023_FilterSign_Reset_command | 4 | 5901 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU023_ErrorCode | 246 | IU023_ErrorCode | 13/0** | 5902 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU023_RemoteControl_Lock | 246 | IU023_RemoteControl_Lock | 19 | 5903 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU023_Occupancy | 246 | IU023_Occupancy | 19 | 5918 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU023_Consumption_Yesterday | 246 | IU023_Consumption_Yesterday | 0 | 5919 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU023_Consumption_Today | 246 | IU023_Consumption_Today | 0 | 5920 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU023_Consumption_Total | 246 | IU023_Consumption_Total | 0 | 5921 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU024_IU_Exist | 246 | IU024_IU_Exist | 3 | 6144 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU024_OnOff_status | 246 | IU024_OnOff_status | 3 | 6145 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU024_OnOff_command | 246 | IU024_OnOff_command | 4 | 6146 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU024_Mode_status | 246 | IU024_Mode_status | 13 | 6147 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU024_Mode_command | 246 | IU024_Mode_command | 14 | 6148 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU024_SetPoint_status | 246 | IU024_SetPoint_status | 0 | 6149 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU024_SetPoint_command | 246 | IU024_SetPoint_command | 1 | 6150 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU024_Room_Temperature | 246 | IU024_Room_Temperature | 0 | 6151 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU024_FanSpeed_status | 246 | IU024_FanSpeed_status | 13 | 6152 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU024_FanSpeed_command | 246 | IU024_FanSpeed_command | 14 | 6153 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU024_AirDirection_status | 246 | IU024_AirDirection_status | 13 | 6154 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU024_AirDirection_command | 246 | IU024_AirDirection_command | 14 | 6155 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU024_FilterSign_status | 246 | IU024_FilterSign_status | 3 | 6156 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU024_FilterSign_Reset_command | 246 | IU024_FilterSign_Reset_command | 4 | 6157 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU024_ErrorCode | 246 | IU024_ErrorCode | 13/0** | 6158 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU024_RemoteControl_Lock | 246 | IU024_RemoteControl_Lock | 19 | 6159 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU024_Occupancy | 246 | IU024_Occupancy | 19 | 6174 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU024_Consumption_Yesterday | 246 | IU024_Consumption_Yesterday | 0 | 6175 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU024_Consumption_Today | 246 | IU024_Consumption_Today | 0 | 6176 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU024_Consumption_Total | 246 | IU024_Consumption_Total | 0 | 6177 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU025_IU_Exist | 246 | IU025_IU_Exist | 3 | 6400 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU025_OnOff_status | 246 | IU025_OnOff_status | 3 | 6401 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU025_OnOff_command | 246 | IU025_OnOff_command | 4 | 6402 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU025_Mode_status | 246 | IU025_Mode_status | 13 | 6403 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU025_Mode_command | 246 | IU025_Mode_command | 14 | 6404 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU025_SetPoint_status | 246 | IU025_SetPoint_status | 0 | 6405 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU025_SetPoint_command | 246 | IU025_SetPoint_command | 1 | 6406 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU025_Room_Temperature | 246 | IU025_Room_Temperature | 0 | 6407 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU025_FanSpeed_status | 246 | IU025_FanSpeed_status | 13 | 6408 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU025_FanSpeed_command | 246 | IU025_FanSpeed_command | 14 | 6409 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU025_AirDirection_status | 246 | IU025_AirDirection_status | 13 | 6410 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU025_AirDirection_command | 246 | IU025_AirDirection_command | 14 | 6411 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU025_FilterSign_status | 246 | IU025_FilterSign_status | 3 | 6412 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU025_FilterSign_Reset_command | 246 | IU025_FilterSign_Reset_command | 4 | 6413 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU025_ErrorCode | 246 | IU025_ErrorCode | 13/0** | 6414 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU025_RemoteControl_Lock | 246 | IU025_RemoteControl_Lock | 19 | 6415 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU025_Occupancy | 246 | IU025_Occupancy | 19 | 6430 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU025_Consumption_Yesterday | 246 | IU025_Consumption_Yesterday | 0 | 6431 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU025_Consumption_Today | 246 | IU025_Consumption_Today | 0 | 6432 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU025_Consumption_Total | 246 | IU025_Consumption_Total | 0 | 6433 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU026_IU_Exist | 246 | IU026_IU_Exist | 3 | 6656 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU026_OnOff_status | 246 | IU026_OnOff_status | 3 | 6657 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU026_OnOff_command | 246 | IU026_OnOff_command | 4 | 6658 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU026_Mode_status | 246 | IU026_Mode_status | 13 | 6659 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU026_Mode_command | 246 | IU026_Mode_command | 14 | 6660 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU026_SetPoint_status | 246 | IU026_SetPoint_status | 0 | 6661 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU026_SetPoint_command | 246 | IU026_SetPoint_command | 1 | 6662 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU026_Room_Temperature | 246 | IU026_Room_Temperature | 0 | 6663 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU026_FanSpeed_status | 246 | IU026_FanSpeed_status | 13 | 6664 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU026_FanSpeed_command | 246 | IU026_FanSpeed_command | 14 | 6665 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU026_AirDirection_status | 246 | IU026_AirDirection_status | 13 | 6666 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU026_AirDirection_command | 246 | IU026_AirDirection_command | 14 | 6667 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU026_FilterSign_status | 246 | IU026_FilterSign_status | 3 | 6668 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU026_FilterSign_Reset_command | 246 | IU026_FilterSign_Reset_command | 4 | 6669 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU026_ErrorCode | 246 | IU026_ErrorCode | 13/0** | 6670 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU026_RemoteControl_Lock | 246 | IU026_RemoteControl_Lock | 19 | 6671 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU026_Occupancy | 246 | IU026_Occupancy | 19 | 6686 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU026_Consumption_Yesterday | 246 | IU026_Consumption_Yesterday | 0 | 6687 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU026_Consumption_Today | 246 | IU026_Consumption_Today | 0 | 6688 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU026_Consumption_Total | 246 | IU026_Consumption_Total | 0 | 6689 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU027_IU_Exist | 246 | IU027_IU_Exist | 3 | 6912 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU027_OnOff_status | 246 | IU027_OnOff_status | 3 | 6913 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU027_OnOff_command | 246 | IU027_OnOff_command | 4 | 6914 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU027_Mode_status | 246 | IU027_Mode_status | 13 | 6915 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU027_Mode_command | 246 | IU027_Mode_command | 14 | 6916 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU027_SetPoint_status | 246 | IU027_SetPoint_status | 0 | 6917 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU027_SetPoint_command | 246 | IU027_SetPoint_command | 1 | 6918 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU027_Room_Temperature | 246 | IU027_Room_Temperature | 0 | 6919 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU027_FanSpeed_status | 246 | IU027_FanSpeed_status | 13 | 6920 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU027_FanSpeed_command | 246 | IU027_FanSpeed_command | 14 | 6921 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU027_AirDirection_status | 246 | IU027_AirDirection_status | 13 | 6922 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU027_AirDirection_command | 246 | IU027_AirDirection_command | 14 | 6923 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU027_FilterSign_status | 246 | IU027_FilterSign_status | 3 | 6924 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU027_FilterSign_Reset_command | 246 | IU027_FilterSign_Reset_command | 4 | 6925 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU027_ErrorCode | 246 | IU027_ErrorCode | 13/0** | 6926 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU027_RemoteControl_Lock | 246 | IU027_RemoteControl_Lock | 19 | 6927 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU027_Occupancy | 246 | IU027_Occupancy | 19 | 6942 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU027_Consumption_Yesterday | 246 | IU027_Consumption_Yesterday | 0 | 6943 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU027_Consumption_Today | 246 | IU027_Consumption_Today | 0 | 6944 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU027_Consumption_Total | 246 | IU027_Consumption_Total | 0 | 6945 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU028_IU_Exist | 246 | IU028_IU_Exist | 3 | 7168 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU028_OnOff_status | 246 | IU028_OnOff_status | 3 | 7169 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU028_OnOff_command | 246 | IU028_OnOff_command | 4 | 7170 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU028_Mode_status | 246 | IU028_Mode_status | 13 | 7171 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU028_Mode_command | 246 | IU028_Mode_command | 14 | 7172 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU028_SetPoint_status | 246 | IU028_SetPoint_status | 0 | 7173 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU028_SetPoint_command | 246 | IU028_SetPoint_command | 1 | 7174 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU028_Room_Temperature | 246 | IU028_Room_Temperature | 0 | 7175 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU028_FanSpeed_status | 246 | IU028_FanSpeed_status | 13 | 7176 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU028_FanSpeed_command | 246 | IU028_FanSpeed_command | 14 | 7177 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU028_AirDirection_status | 246 | IU028_AirDirection_status | 13 | 7178 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU028_AirDirection_command | 246 | IU028_AirDirection_command | 14 | 7179 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU028_FilterSign_status | 246 | IU028_FilterSign_status | 3 | 7180 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU028_FilterSign_Reset_command | 246 | IU028_FilterSign_Reset_command | 4 | 7181 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU028_ErrorCode | 246 | IU028_ErrorCode | 13/0** | 7182 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU028_RemoteControl_Lock | 246 | IU028_RemoteControl_Lock | 19 | 7183 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU028_Occupancy | 246 | IU028_Occupancy | 19 | 7198 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU028_Consumption_Yesterday | 246 | IU028_Consumption_Yesterday | 0 | 7199 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU028_Consumption_Today | 246 | IU028_Consumption_Today | 0 | 7200 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU028_Consumption_Total | 246 | IU028_Consumption_Total | 0 | 7201 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU029_IU_Exist | 246 | IU029_IU_Exist | 3 | 7424 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU029_OnOff_status | 246 | IU029_OnOff_status | 3 | 7425 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU029_OnOff_command | 246 | IU029_OnOff_command | 4 | 7426 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU029_Mode_status | 246 | IU029_Mode_status | 13 | 7427 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU029_Mode_command | 246 | IU029_Mode_command | 14 | 7428 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU029_SetPoint_status | 246 | IU029_SetPoint_status | 0 | 7429 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU029_SetPoint_command | 246 | IU029_SetPoint_command | 1 | 7430 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU029_Room_Temperature | 246 | IU029_Room_Temperature | 0 | 7431 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU029_FanSpeed_status | 246 | IU029_FanSpeed_status | 13 | 7432 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU029_FanSpeed_command | 246 | IU029_FanSpeed_command | 14 | 7433 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU029_AirDirection_status | 246 | IU029_AirDirection_status | 13 | 7434 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU029_AirDirection_command | 246 | IU029_AirDirection_command | 14 | 7435 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU029_FilterSign_status | 246 | IU029_FilterSign_status | 3 | 7436 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU029_FilterSign_Reset_command | 246 | IU029_FilterSign_Reset_command | 4 | 7437 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU029_ErrorCode | 246 | IU029_ErrorCode | 13/0** | 7438 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU029_RemoteControl_Lock | 246 | IU029_RemoteControl_Lock | 19 | 7439 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU029_Occupancy | 246 | IU029_Occupancy | 19 | 7454 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU029_Consumption_Yesterday | 246 | IU029_Consumption_Yesterday | 0 | 7455 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU029_Consumption_Today | 246 | IU029_Consumption_Today | 0 | 7456 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU029_Consumption_Total | 246 | IU029_Consumption_Total | 0 | 7457 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU030_IU_Exist | 246 | IU030_IU_Exist | 3 | 7680 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU030_OnOff_status | 246 | IU030_OnOff_status | 3 | 7681 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU030_OnOff_command | 246 | IU030_OnOff_command | 4 | 7682 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU030_Mode_status | 246 | IU030_Mode_status | 13 | 7683 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU030_Mode_command | 246 | IU030_Mode_command | 14 | 7684 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU030_SetPoint_status | 246 | IU030_SetPoint_status | 0 | 7685 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU030_SetPoint_command | 246 | IU030_SetPoint_command | 1 | 7686 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU030_Room_Temperature | 246 | IU030_Room_Temperature | 0 | 7687 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU030_FanSpeed_status | 246 | IU030_FanSpeed_status | 13 | 7688 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU030_FanSpeed_command | 246 | IU030_FanSpeed_command | 14 | 7689 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU030_AirDirection_status | 246 | IU030_AirDirection_status | 13 | 7690 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU030_AirDirection_command | 246 | IU030_AirDirection_command | 14 | 7691 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU030_FilterSign_status | 246 | IU030_FilterSign_status | 3 | 7692 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU030_FilterSign_Reset_command | 246 | IU030_FilterSign_Reset_command | 4 | 7693 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU030_ErrorCode | 246 | IU030_ErrorCode | 13/0** | 7694 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU030_RemoteControl_Lock | 246 | IU030_RemoteControl_Lock | 19 | 7695 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU030_Occupancy | 246 | IU030_Occupancy | 19 | 7710 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU030_Consumption_Yesterday | 246 | IU030_Consumption_Yesterday | 0 | 7711 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU030_Consumption_Today | 246 | IU030_Consumption_Today | 0 | 7712 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU030_Consumption_Total | 246 | IU030_Consumption_Total | 0 | 7713 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU031_IU_Exist | 246 | IU031_IU_Exist | 3 | 7936 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU031_OnOff_status | 246 | IU031_OnOff_status | 3 | 7937 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU031_OnOff_command | 246 | IU031_OnOff_command | 4 | 7938 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU031_Mode_status | 246 | IU031_Mode_status | 13 | 7939 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU031_Mode_command | 246 | IU031_Mode_command | 14 | 7940 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU031_SetPoint_status | 246 | IU031_SetPoint_status | 0 | 7941 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU031_SetPoint_command | 246 | IU031_SetPoint_command | 1 | 7942 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU031_Room_Temperature | 246 | IU031_Room_Temperature | 0 | 7943 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU031_FanSpeed_status | 246 | IU031_FanSpeed_status | 13 | 7944 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU031_FanSpeed_command | 246 | IU031_FanSpeed_command | 14 | 7945 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU031_AirDirection_status | 246 | IU031_AirDirection_status | 13 | 7946 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU031_AirDirection_command | 246 | IU031_AirDirection_command | 14 | 7947 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU031_FilterSign_status | 246 | IU031_FilterSign_status | 3 | 7948 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU031_FilterSign_Reset_command | 246 | IU031_FilterSign_Reset_command | 4 | 7949 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU031_ErrorCode | 246 | IU031_ErrorCode | 13/0** | 7950 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU031_RemoteControl_Lock | 246 | IU031_RemoteControl_Lock | 19 | 7951 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU031_Occupancy | 246 | IU031_Occupancy | 19 | 7966 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU031_Consumption_Yesterday | 246 | IU031_Consumption_Yesterday | 0 | 7967 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU031_Consumption_Today | 246 | IU031_Consumption_Today | 0 | 7968 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU031_Consumption_Total | 246 | IU031_Consumption_Total | 0 | 7969 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU032_IU_Exist | 246 | IU032_IU_Exist | 3 | 8192 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU032_OnOff_status | 246 | IU032_OnOff_status | 3 | 8193 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU032_OnOff_command | 246 | IU032_OnOff_command | 4 | 8194 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU032_Mode_status | 246 | IU032_Mode_status | 13 | 8195 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU032_Mode_command | 246 | IU032_Mode_command | 14 | 8196 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU032_SetPoint_status | 246 | IU032_SetPoint_status | 0 | 8197 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU032_SetPoint_command | 246 | IU032_SetPoint_command | 1 | 8198 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU032_Room_Temperature | 246 | IU032_Room_Temperature | 0 | 8199 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU032_FanSpeed_status | 246 | IU032_FanSpeed_status | 13 | 8200 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU032_FanSpeed_command | 246 | IU032_FanSpeed_command | 14 | 8201 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU032_AirDirection_status | 246 | IU032_AirDirection_status | 13 | 8202 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU032_AirDirection_command | 246 | IU032_AirDirection_command | 14 | 8203 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU032_FilterSign_status | 246 | IU032_FilterSign_status | 3 | 8204 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU032_FilterSign_Reset_command | 246 | IU032_FilterSign_Reset_command | 4 | 8205 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU032_ErrorCode | 246 | IU032_ErrorCode | 13/0** | 8206 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU032_RemoteControl_Lock | 246 | IU032_RemoteControl_Lock | 19 | 8207 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU032_Occupancy | 246 | IU032_Occupancy | 19 | 8222 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU032_Consumption_Yesterday | 246 | IU032_Consumption_Yesterday | 0 | 8223 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU032_Consumption_Today | 246 | IU032_Consumption_Today | 0 | 8224 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU032_Consumption_Total | 246 | IU032_Consumption_Total | 0 | 8225 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU033_IU_Exist | 246 | IU033_IU_Exist | 3 | 8448 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU033_OnOff_status | 246 | IU033_OnOff_status | 3 | 8449 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU033_OnOff_command | 246 | IU033_OnOff_command | 4 | 8450 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU033_Mode_status | 246 | IU033_Mode_status | 13 | 8451 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU033_Mode_command | 246 | IU033_Mode_command | 14 | 8452 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU033_SetPoint_status | 246 | IU033_SetPoint_status | 0 | 8453 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU033_SetPoint_command | 246 | IU033_SetPoint_command | 1 | 8454 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU033_Room_Temperature | 246 | IU033_Room_Temperature | 0 | 8455 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU033_FanSpeed_status | 246 | IU033_FanSpeed_status | 13 | 8456 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU033_FanSpeed_command | 246 | IU033_FanSpeed_command | 14 | 8457 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU033_AirDirection_status | 246 | IU033_AirDirection_status | 13 | 8458 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU033_AirDirection_command | 246 | IU033_AirDirection_command | 14 | 8459 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU033_FilterSign_status | 246 | IU033_FilterSign_status | 3 | 8460 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU033_FilterSign_Reset_command | 246 | IU033_FilterSign_Reset_command | 4 | 8461 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU033_ErrorCode | 246 | IU033_ErrorCode | 13/0** | 8462 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU033_RemoteControl_Lock | 246 | IU033_RemoteControl_Lock | 19 | 8463 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU033_Occupancy | 246 | IU033_Occupancy | 19 | 8478 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU033_Consumption_Yesterday | 246 | IU033_Consumption_Yesterday | 0 | 8479 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU033_Consumption_Today | 246 | IU033_Consumption_Today | 0 | 8480 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU033_Consumption_Total | 246 | IU033_Consumption_Total | 0 | 8481 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU034_IU_Exist | 246 | IU034_IU_Exist | 3 | 8704 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU034_OnOff_status | 246 | IU034_OnOff_status | 3 | 8705 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU034_OnOff_command | 246 | IU034_OnOff_command | 4 | 8706 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU034_Mode_status | 246 | IU034_Mode_status | 13 | 8707 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU034_Mode_command | 246 | IU034_Mode_command | 14 | 8708 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU034_SetPoint_status | 246 | IU034_SetPoint_status | 0 | 8709 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU034_SetPoint_command | 246 | IU034_SetPoint_command | 1 | 8710 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU034_Room_Temperature | 246 | IU034_Room_Temperature | 0 | 8711 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU034_FanSpeed_status | 246 | IU034_FanSpeed_status | 13 | 8712 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU034_FanSpeed_command | 246 | IU034_FanSpeed_command | 14 | 8713 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU034_AirDirection_status | 246 | IU034_AirDirection_status | 13 | 8714 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU034_AirDirection_command | 246 | IU034_AirDirection_command | 14 | 8715 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU034_FilterSign_status | 246 | IU034_FilterSign_status | 3 | 8716 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU034_FilterSign_Reset_command | 246 | IU034_FilterSign_Reset_command | 4 | 8717 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU034_ErrorCode | 246 | IU034_ErrorCode | 13/0** | 8718 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU034_RemoteControl_Lock | 246 | IU034_RemoteControl_Lock | 19 | 8719 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU034_Occupancy | 246 | IU034_Occupancy | 19 | 8734 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU034_Consumption_Yesterday | 246 | IU034_Consumption_Yesterday | 0 | 8735 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU034_Consumption_Today | 246 | IU034_Consumption_Today | 0 | 8736 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU034_Consumption_Total | 246 | IU034_Consumption_Total | 0 | 8737 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU035_IU_Exist | 246 | IU035_IU_Exist | 3 | 8960 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU035_OnOff_status | 246 | IU035_OnOff_status | 3 | 8961 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU035_OnOff_command | 246 | IU035_OnOff_command | 4 | 8962 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU035_Mode_status | 246 | IU035_Mode_status | 13 | 8963 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU035_Mode_command | 246 | IU035_Mode_command | 14 | 8964 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU035_SetPoint_status | 246 | IU035_SetPoint_status | 0 | 8965 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU035_SetPoint_command | 246 | IU035_SetPoint_command | 1 | 8966 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU035_Room_Temperature | 246 | IU035_Room_Temperature | 0 | 8967 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU035_FanSpeed_status | 246 | IU035_FanSpeed_status | 13 | 8968 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU035_FanSpeed_command | 246 | IU035_FanSpeed_command | 14 | 8969 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU035_AirDirection_status | 246 | IU035_AirDirection_status | 13 | 8970 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU035_AirDirection_command | 246 | IU035_AirDirection_command | 14 | 8971 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU035_FilterSign_status | 246 | IU035_FilterSign_status | 3 | 8972 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU035_FilterSign_Reset_command | 246 | IU035_FilterSign_Reset_command | 4 | 8973 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU035_ErrorCode | 246 | IU035_ErrorCode | 13/0** | 8974 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU035_RemoteControl_Lock | 246 | IU035_RemoteControl_Lock | 19 | 8975 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU035_Occupancy | 246 | IU035_Occupancy | 19 | 8990 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU035_Consumption_Yesterday | 246 | IU035_Consumption_Yesterday | 0 | 8991 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU035_Consumption_Today | 246 | IU035_Consumption_Today | 0 | 8992 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU035_Consumption_Total | 246 | IU035_Consumption_Total | 0 | 8993 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU036_IU_Exist | 246 | IU036_IU_Exist | 3 | 9216 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU036_OnOff_status | 246 | IU036_OnOff_status | 3 | 9217 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU036_OnOff_command | 246 | IU036_OnOff_command | 4 | 9218 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU036_Mode_status | 246 | IU036_Mode_status | 13 | 9219 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU036_Mode_command | 246 | IU036_Mode_command | 14 | 9220 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU036_SetPoint_status | 246 | IU036_SetPoint_status | 0 | 9221 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU036_SetPoint_command | 246 | IU036_SetPoint_command | 1 | 9222 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU036_Room_Temperature | 246 | IU036_Room_Temperature | 0 | 9223 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU036_FanSpeed_status | 246 | IU036_FanSpeed_status | 13 | 9224 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU036_FanSpeed_command | 246 | IU036_FanSpeed_command | 14 | 9225 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU036_AirDirection_status | 246 | IU036_AirDirection_status | 13 | 9226 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU036_AirDirection_command | 246 | IU036_AirDirection_command | 14 | 9227 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU036_FilterSign_status | 246 | IU036_FilterSign_status | 3 | 9228 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU036_FilterSign_Reset_command | 246 | IU036_FilterSign_Reset_command | 4 | 9229 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU036_ErrorCode | 246 | IU036_ErrorCode | 13/0** | 9230 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU036_RemoteControl_Lock | 246 | IU036_RemoteControl_Lock | 19 | 9231 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU036_Occupancy | 246 | IU036_Occupancy | 19 | 9246 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU036_Consumption_Yesterday | 246 | IU036_Consumption_Yesterday | 0 | 9247 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU036_Consumption_Today | 246 | IU036_Consumption_Today | 0 | 9248 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU036_Consumption_Total | 246 | IU036_Consumption_Total | 0 | 9249 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU037_IU_Exist | 246 | IU037_IU_Exist | 3 | 9472 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU037_OnOff_status | 246 | IU037_OnOff_status | 3 | 9473 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU037_OnOff_command | 246 | IU037_OnOff_command | 4 | 9474 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU037_Mode_status | 246 | IU037_Mode_status | 13 | 9475 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU037_Mode_command | 246 | IU037_Mode_command | 14 | 9476 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU037_SetPoint_status | 246 | IU037_SetPoint_status | 0 | 9477 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU037_SetPoint_command | 246 | IU037_SetPoint_command | 1 | 9478 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU037_Room_Temperature | 246 | IU037_Room_Temperature | 0 | 9479 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU037_FanSpeed_status | 246 | IU037_FanSpeed_status | 13 | 9480 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU037_FanSpeed_command | 246 | IU037_FanSpeed_command | 14 | 9481 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU037_AirDirection_status | 246 | IU037_AirDirection_status | 13 | 9482 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU037_AirDirection_command | 246 | IU037_AirDirection_command | 14 | 9483 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU037_FilterSign_status | 246 | IU037_FilterSign_status | 3 | 9484 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU037_FilterSign_Reset_command | 246 | IU037_FilterSign_Reset_command | 4 | 9485 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU037_ErrorCode | 246 | IU037_ErrorCode | 13/0** | 9486 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU037_RemoteControl_Lock | 246 | IU037_RemoteControl_Lock | 19 | 9487 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU037_Occupancy | 246 | IU037_Occupancy | 19 | 9502 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU037_Consumption_Yesterday | 246 | IU037_Consumption_Yesterday | 0 | 9503 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU037_Consumption_Today | 246 | IU037_Consumption_Today | 0 | 9504 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU037_Consumption_Total | 246 | IU037_Consumption_Total | 0 | 9505 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU038_IU_Exist | 246 | IU038_IU_Exist | 3 | 9728 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU038_OnOff_status | 246 | IU038_OnOff_status | 3 | 9729 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU038_OnOff_command | 246 | IU038_OnOff_command | 4 | 9730 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU038_Mode_status | 246 | IU038_Mode_status | 13 | 9731 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU038_Mode_command | 246 | IU038_Mode_command | 14 | 9732 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU038_SetPoint_status | 246 | IU038_SetPoint_status | 0 | 9733 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU038_SetPoint_command | 246 | IU038_SetPoint_command | 1 | 9734 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU038_Room_Temperature | 246 | IU038_Room_Temperature | 0 | 9735 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU038_FanSpeed_status | 246 | IU038_FanSpeed_status | 13 | 9736 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU038_FanSpeed_command | 246 | IU038_FanSpeed_command | 14 | 9737 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU038_AirDirection_status | 246 | IU038_AirDirection_status | 13 | 9738 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU038_AirDirection_command | 246 | IU038_AirDirection_command | 14 | 9739 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU038_FilterSign_status | 246 | IU038_FilterSign_status | 3 | 9740 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU038_FilterSign_Reset_command | 246 | IU038_FilterSign_Reset_command | 4 | 9741 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU038_ErrorCode | 246 | IU038_ErrorCode | 13/0** | 9742 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU038_RemoteControl_Lock | 246 | IU038_RemoteControl_Lock | 19 | 9743 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU038_Occupancy | 246 | IU038_Occupancy | 19 | 9758 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU038_Consumption_Yesterday | 246 | IU038_Consumption_Yesterday | 0 | 9759 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU038_Consumption_Today | 246 | IU038_Consumption_Today | 0 | 9760 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU038_Consumption_Total | 246 | IU038_Consumption_Total | 0 | 9761 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU039_IU_Exist | 246 | IU039_IU_Exist | 3 | 9984 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU039_OnOff_status | 246 | IU039_OnOff_status | 3 | 9985 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU039_OnOff_command | 246 | IU039_OnOff_command | 4 | 9986 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU039_Mode_status | 246 | IU039_Mode_status | 13 | 9987 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU039_Mode_command | 246 | IU039_Mode_command | 14 | 9988 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU039_SetPoint_status | 246 | IU039_SetPoint_status | 0 | 9989 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU039_SetPoint_command | 246 | IU039_SetPoint_command | 1 | 9990 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU039_Room_Temperature | 246 | IU039_Room_Temperature | 0 | 9991 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU039_FanSpeed_status | 246 | IU039_FanSpeed_status | 13 | 9992 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU039_FanSpeed_command | 246 | IU039_FanSpeed_command | 14 | 9993 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU039_AirDirection_status | 246 | IU039_AirDirection_status | 13 | 9994 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU039_AirDirection_command | 246 | IU039_AirDirection_command | 14 | 9995 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU039_FilterSign_status | 246 | IU039_FilterSign_status | 3 | 9996 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU039_FilterSign_Reset_command | 246 | IU039_FilterSign_Reset_command | 4 | 9997 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU039_ErrorCode | 246 | IU039_ErrorCode | 13/0** | 9998 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU039_RemoteControl_Lock | 246 | IU039_RemoteControl_Lock | 19 | 9999 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU039_Occupancy | 246 | IU039_Occupancy | 19 | 10014 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU039_Consumption_Yesterday | 246 | IU039_Consumption_Yesterday | 0 | 10015 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU039_Consumption_Today | 246 | IU039_Consumption_Today | 0 | 10016 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU039_Consumption_Total | 246 | IU039_Consumption_Total | 0 | 10017 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU040_IU_Exist | 246 | IU040_IU_Exist | 3 | 10240 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU040_OnOff_status | 246 | IU040_OnOff_status | 3 | 10241 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU040_OnOff_command | 246 | IU040_OnOff_command | 4 | 10242 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU040_Mode_status | 246 | IU040_Mode_status | 13 | 10243 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU040_Mode_command | 246 | IU040_Mode_command | 14 | 10244 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU040_SetPoint_status | 246 | IU040_SetPoint_status | 0 | 10245 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU040_SetPoint_command | 246 | IU040_SetPoint_command | 1 | 10246 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU040_Room_Temperature | 246 | IU040_Room_Temperature | 0 | 10247 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU040_FanSpeed_status | 246 | IU040_FanSpeed_status | 13 | 10248 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU040_FanSpeed_command | 246 | IU040_FanSpeed_command | 14 | 10249 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU040_AirDirection_status | 246 | IU040_AirDirection_status | 13 | 10250 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU040_AirDirection_command | 246 | IU040_AirDirection_command | 14 | 10251 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU040_FilterSign_status | 246 | IU040_FilterSign_status | 3 | 10252 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU040_FilterSign_Reset_command | 246 | IU040_FilterSign_Reset_command | 4 | 10253 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU040_ErrorCode | 246 | IU040_ErrorCode | 13/0** | 10254 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU040_RemoteControl_Lock | 246 | IU040_RemoteControl_Lock | 19 | 10255 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU040_Occupancy | 246 | IU040_Occupancy | 19 | 10270 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU040_Consumption_Yesterday | 246 | IU040_Consumption_Yesterday | 0 | 10271 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU040_Consumption_Today | 246 | IU040_Consumption_Today | 0 | 10272 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU040_Consumption_Total | 246 | IU040_Consumption_Total | 0 | 10273 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU041_IU_Exist | 246 | IU041_IU_Exist | 3 | 10496 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU041_OnOff_status | 246 | IU041_OnOff_status | 3 | 10497 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU041_OnOff_command | 246 | IU041_OnOff_command | 4 | 10498 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU041_Mode_status | 246 | IU041_Mode_status | 13 | 10499 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU041_Mode_command | 246 | IU041_Mode_command | 14 | 10500 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU041_SetPoint_status | 246 | IU041_SetPoint_status | 0 | 10501 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU041_SetPoint_command | 246 | IU041_SetPoint_command | 1 | 10502 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU041_Room_Temperature | 246 | IU041_Room_Temperature | 0 | 10503 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU041_FanSpeed_status | 246 | IU041_FanSpeed_status | 13 | 10504 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU041_FanSpeed_command | 246 | IU041_FanSpeed_command | 14 | 10505 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU041_AirDirection_status | 246 | IU041_AirDirection_status | 13 | 10506 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU041_AirDirection_command | 246 | IU041_AirDirection_command | 14 | 10507 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU041_FilterSign_status | 246 | IU041_FilterSign_status | 3 | 10508 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU041_FilterSign_Reset_command | 246 | IU041_FilterSign_Reset_command | 4 | 10509 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU041_ErrorCode | 246 | IU041_ErrorCode | 13/0** | 10510 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU041_RemoteControl_Lock | 246 | IU041_RemoteControl_Lock | 19 | 10511 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU041_Occupancy | 246 | IU041_Occupancy | 19 | 10526 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU041_Consumption_Yesterday | 246 | IU041_Consumption_Yesterday | 0 | 10527 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU041_Consumption_Today | 246 | IU041_Consumption_Today | 0 | 10528 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU041_Consumption_Total | 246 | IU041_Consumption_Total | 0 | 10529 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU042_IU_Exist | 246 | IU042_IU_Exist | 3 | 10752 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU042_OnOff_status | 246 | IU042_OnOff_status | 3 | 10753 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU042_OnOff_command | 246 | IU042_OnOff_command | 4 | 10754 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU042_Mode_status | 246 | IU042_Mode_status | 13 | 10755 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU042_Mode_command | 246 | IU042_Mode_command | 14 | 10756 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU042_SetPoint_status | 246 | IU042_SetPoint_status | 0 | 10757 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU042_SetPoint_command | 246 | IU042_SetPoint_command | 1 | 10758 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU042_Room_Temperature | 246 | IU042_Room_Temperature | 0 | 10759 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU042_FanSpeed_status | 246 | IU042_FanSpeed_status | 13 | 10760 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU042_FanSpeed_command | 246 | IU042_FanSpeed_command | 14 | 10761 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU042_AirDirection_status | 246 | IU042_AirDirection_status | 13 | 10762 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU042_AirDirection_command | 246 | IU042_AirDirection_command | 14 | 10763 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU042_FilterSign_status | 246 | IU042_FilterSign_status | 3 | 10764 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU042_FilterSign_Reset_command | 246 | IU042_FilterSign_Reset_command | 4 | 10765 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU042_ErrorCode | 246 | IU042_ErrorCode | 13/0** | 10766 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU042_RemoteControl_Lock | 246 | IU042_RemoteControl_Lock | 19 | 10767 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU042_Occupancy | 246 | IU042_Occupancy | 19 | 10782 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU042_Consumption_Yesterday | 246 | IU042_Consumption_Yesterday | 0 | 10783 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU042_Consumption_Today | 246 | IU042_Consumption_Today | 0 | 10784 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU042_Consumption_Total | 246 | IU042_Consumption_Total | 0 | 10785 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU043_IU_Exist | 246 | IU043_IU_Exist | 3 | 11008 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU043_OnOff_status | 246 | IU043_OnOff_status | 3 | 11009 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU043_OnOff_command | 246 | IU043_OnOff_command | 4 | 11010 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU043_Mode_status | 246 | IU043_Mode_status | 13 | 11011 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU043_Mode_command | 246 | IU043_Mode_command | 14 | 11012 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU043_SetPoint_status | 246 | IU043_SetPoint_status | 0 | 11013 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU043_SetPoint_command | 246 | IU043_SetPoint_command | 1 | 11014 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU043_Room_Temperature | 246 | IU043_Room_Temperature | 0 | 11015 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU043_FanSpeed_status | 246 | IU043_FanSpeed_status | 13 | 11016 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU043_FanSpeed_command | 246 | IU043_FanSpeed_command | 14 | 11017 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU043_AirDirection_status | 246 | IU043_AirDirection_status | 13 | 11018 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU043_AirDirection_command | 246 | IU043_AirDirection_command | 14 | 11019 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU043_FilterSign_status | 246 | IU043_FilterSign_status | 3 | 11020 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU043_FilterSign_Reset_command | 246 | IU043_FilterSign_Reset_command | 4 | 11021 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU043_ErrorCode | 246 | IU043_ErrorCode | 13/0** | 11022 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU043_RemoteControl_Lock | 246 | IU043_RemoteControl_Lock | 19 | 11023 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU043_Occupancy | 246 | IU043_Occupancy | 19 | 11038 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU043_Consumption_Yesterday | 246 | IU043_Consumption_Yesterday | 0 | 11039 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU043_Consumption_Today | 246 | IU043_Consumption_Today | 0 | 11040 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU043_Consumption_Total | 246 | IU043_Consumption_Total | 0 | 11041 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU044_IU_Exist | 246 | IU044_IU_Exist | 3 | 11264 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU044_OnOff_status | 246 | IU044_OnOff_status | 3 | 11265 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU044_OnOff_command | 246 | IU044_OnOff_command | 4 | 11266 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU044_Mode_status | 246 | IU044_Mode_status | 13 | 11267 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU044_Mode_command | 246 | IU044_Mode_command | 14 | 11268 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU044_SetPoint_status | 246 | IU044_SetPoint_status | 0 | 11269 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU044_SetPoint_command | 246 | IU044_SetPoint_command | 1 | 11270 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU044_Room_Temperature | 246 | IU044_Room_Temperature | 0 | 11271 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU044_FanSpeed_status | 246 | IU044_FanSpeed_status | 13 | 11272 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU044_FanSpeed_command | 246 | IU044_FanSpeed_command | 14 | 11273 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU044_AirDirection_status | 246 | IU044_AirDirection_status | 13 | 11274 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU044_AirDirection_command | 246 | IU044_AirDirection_command | 14 | 11275 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU044_FilterSign_status | 246 | IU044_FilterSign_status | 3 | 11276 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU044_FilterSign_Reset_command | 246 | IU044_FilterSign_Reset_command | 4 | 11277 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU044_ErrorCode | 246 | IU044_ErrorCode | 13/0** | 11278 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU044_RemoteControl_Lock | 246 | IU044_RemoteControl_Lock | 19 | 11279 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU044_Occupancy | 246 | IU044_Occupancy | 19 | 11294 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU044_Consumption_Yesterday | 246 | IU044_Consumption_Yesterday | 0 | 11295 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU044_Consumption_Today | 246 | IU044_Consumption_Today | 0 | 11296 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU044_Consumption_Total | 246 | IU044_Consumption_Total | 0 | 11297 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU045_IU_Exist | 246 | IU045_IU_Exist | 3 | 11520 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU045_OnOff_status | 246 | IU045_OnOff_status | 3 | 11521 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU045_OnOff_command | 246 | IU045_OnOff_command | 4 | 11522 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU045_Mode_status | 246 | IU045_Mode_status | 13 | 11523 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU045_Mode_command | 246 | IU045_Mode_command | 14 | 11524 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU045_SetPoint_status | 246 | IU045_SetPoint_status | 0 | 11525 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU045_SetPoint_command | 246 | IU045_SetPoint_command | 1 | 11526 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU045_Room_Temperature | 246 | IU045_Room_Temperature | 0 | 11527 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU045_FanSpeed_status | 246 | IU045_FanSpeed_status | 13 | 11528 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU045_FanSpeed_command | 246 | IU045_FanSpeed_command | 14 | 11529 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU045_AirDirection_status | 246 | IU045_AirDirection_status | 13 | 11530 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU045_AirDirection_command | 246 | IU045_AirDirection_command | 14 | 11531 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU045_FilterSign_status | 246 | IU045_FilterSign_status | 3 | 11532 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU045_FilterSign_Reset_command | 246 | IU045_FilterSign_Reset_command | 4 | 11533 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU045_ErrorCode | 246 | IU045_ErrorCode | 13/0** | 11534 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU045_RemoteControl_Lock | 246 | IU045_RemoteControl_Lock | 19 | 11535 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU045_Occupancy | 246 | IU045_Occupancy | 19 | 11550 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU045_Consumption_Yesterday | 246 | IU045_Consumption_Yesterday | 0 | 11551 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU045_Consumption_Today | 246 | IU045_Consumption_Today | 0 | 11552 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU045_Consumption_Total | 246 | IU045_Consumption_Total | 0 | 11553 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU046_IU_Exist | 246 | IU046_IU_Exist | 3 | 11776 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU046_OnOff_status | 246 | IU046_OnOff_status | 3 | 11777 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU046_OnOff_command | 246 | IU046_OnOff_command | 4 | 11778 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU046_Mode_status | 246 | IU046_Mode_status | 13 | 11779 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU046_Mode_command | 246 | IU046_Mode_command | 14 | 11780 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU046_SetPoint_status | 246 | IU046_SetPoint_status | 0 | 11781 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU046_SetPoint_command | 246 | IU046_SetPoint_command | 1 | 11782 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU046_Room_Temperature | 246 | IU046_Room_Temperature | 0 | 11783 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU046_FanSpeed_status | 246 | IU046_FanSpeed_status | 13 | 11784 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU046_FanSpeed_command | 246 | IU046_FanSpeed_command | 14 | 11785 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU046_AirDirection_status | 246 | IU046_AirDirection_status | 13 | 11786 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU046_AirDirection_command | 246 | IU046_AirDirection_command | 14 | 11787 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU046_FilterSign_status | 246 | IU046_FilterSign_status | 3 | 11788 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU046_FilterSign_Reset_command | 246 | IU046_FilterSign_Reset_command | 4 | 11789 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU046_ErrorCode | 246 | IU046_ErrorCode | 13/0** | 11790 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU046_RemoteControl_Lock | 246 | IU046_RemoteControl_Lock | 19 | 11791 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU046_Occupancy | 246 | IU046_Occupancy | 19 | 11806 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU046_Consumption_Yesterday | 246 | IU046_Consumption_Yesterday | 0 | 11807 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU046_Consumption_Today | 246 | IU046_Consumption_Today | 0 | 11808 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU046_Consumption_Total | 246 | IU046_Consumption_Total | 0 | 11809 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU047_IU_Exist | 246 | IU047_IU_Exist | 3 | 12032 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU047_OnOff_status | 246 | IU047_OnOff_status | 3 | 12033 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU047_OnOff_command | 246 | IU047_OnOff_command | 4 | 12034 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU047_Mode_status | 246 | IU047_Mode_status | 13 | 12035 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU047_Mode_command | 246 | IU047_Mode_command | 14 | 12036 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU047_SetPoint_status | 246 | IU047_SetPoint_status | 0 | 12037 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU047_SetPoint_command | 246 | IU047_SetPoint_command | 1 | 12038 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU047_Room_Temperature | 246 | IU047_Room_Temperature | 0 | 12039 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU047_FanSpeed_status | 246 | IU047_FanSpeed_status | 13 | 12040 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU047_FanSpeed_command | 246 | IU047_FanSpeed_command | 14 | 12041 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU047_AirDirection_status | 246 | IU047_AirDirection_status | 13 | 12042 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU047_AirDirection_command | 246 | IU047_AirDirection_command | 14 | 12043 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU047_FilterSign_status | 246 | IU047_FilterSign_status | 3 | 12044 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU047_FilterSign_Reset_command | 246 | IU047_FilterSign_Reset_command | 4 | 12045 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU047_ErrorCode | 246 | IU047_ErrorCode | 13/0** | 12046 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU047_RemoteControl_Lock | 246 | IU047_RemoteControl_Lock | 19 | 12047 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU047_Occupancy | 246 | IU047_Occupancy | 19 | 12062 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU047_Consumption_Yesterday | 246 | IU047_Consumption_Yesterday | 0 | 12063 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU047_Consumption_Today | 246 | IU047_Consumption_Today | 0 | 12064 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU047_Consumption_Total | 246 | IU047_Consumption_Total | 0 | 12065 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU048_IU_Exist | 246 | IU048_IU_Exist | 3 | 12288 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU048_OnOff_status | 246 | IU048_OnOff_status | 3 | 12289 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU048_OnOff_command | 246 | IU048_OnOff_command | 4 | 12290 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU048_Mode_status | 246 | IU048_Mode_status | 13 | 12291 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU048_Mode_command | 246 | IU048_Mode_command | 14 | 12292 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU048_SetPoint_status | 246 | IU048_SetPoint_status | 0 | 12293 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU048_SetPoint_command | 246 | IU048_SetPoint_command | 1 | 12294 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU048_Room_Temperature | 246 | IU048_Room_Temperature | 0 | 12295 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU048_FanSpeed_status | 246 | IU048_FanSpeed_status | 13 | 12296 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU048_FanSpeed_command | 246 | IU048_FanSpeed_command | 14 | 12297 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU048_AirDirection_status | 246 | IU048_AirDirection_status | 13 | 12298 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU048_AirDirection_command | 246 | IU048_AirDirection_command | 14 | 12299 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU048_FilterSign_status | 246 | IU048_FilterSign_status | 3 | 12300 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU048_FilterSign_Reset_command | 246 | IU048_FilterSign_Reset_command | 4 | 12301 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU048_ErrorCode | 246 | IU048_ErrorCode | 13/0** | 12302 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU048_RemoteControl_Lock | 246 | IU048_RemoteControl_Lock | 19 | 12303 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU048_Occupancy | 246 | IU048_Occupancy | 19 | 12318 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU048_Consumption_Yesterday | 246 | IU048_Consumption_Yesterday | 0 | 12319 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU048_Consumption_Today | 246 | IU048_Consumption_Today | 0 | 12320 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU048_Consumption_Total | 246 | IU048_Consumption_Total | 0 | 12321 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU049_IU_Exist | 246 | IU049_IU_Exist | 3 | 12544 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU049_OnOff_status | 246 | IU049_OnOff_status | 3 | 12545 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU049_OnOff_command | 246 | IU049_OnOff_command | 4 | 12546 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU049_Mode_status | 246 | IU049_Mode_status | 13 | 12547 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU049_Mode_command | 246 | IU049_Mode_command | 14 | 12548 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU049_SetPoint_status | 246 | IU049_SetPoint_status | 0 | 12549 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU049_SetPoint_command | 246 | IU049_SetPoint_command | 1 | 12550 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU049_Room_Temperature | 246 | IU049_Room_Temperature | 0 | 12551 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU049_FanSpeed_status | 246 | IU049_FanSpeed_status | 13 | 12552 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU049_FanSpeed_command | 246 | IU049_FanSpeed_command | 14 | 12553 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU049_AirDirection_status | 246 | IU049_AirDirection_status | 13 | 12554 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU049_AirDirection_command | 246 | IU049_AirDirection_command | 14 | 12555 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU049_FilterSign_status | 246 | IU049_FilterSign_status | 3 | 12556 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU049_FilterSign_Reset_command | 246 | IU049_FilterSign_Reset_command | 4 | 12557 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU049_ErrorCode | 246 | IU049_ErrorCode | 13/0** | 12558 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU049_RemoteControl_Lock | 246 | IU049_RemoteControl_Lock | 19 | 12559 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU049_Occupancy | 246 | IU049_Occupancy | 19 | 12574 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU049_Consumption_Yesterday | 246 | IU049_Consumption_Yesterday | 0 | 12575 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU049_Consumption_Today | 246 | IU049_Consumption_Today | 0 | 12576 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU049_Consumption_Total | 246 | IU049_Consumption_Total | 0 | 12577 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU050_IU_Exist | 246 | IU050_IU_Exist | 3 | 12800 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU050_OnOff_status | 246 | IU050_OnOff_status | 3 | 12801 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU050_OnOff_command | 246 | IU050_OnOff_command | 4 | 12802 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU050_Mode_status | 246 | IU050_Mode_status | 13 | 12803 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU050_Mode_command | 246 | IU050_Mode_command | 14 | 12804 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU050_SetPoint_status | 246 | IU050_SetPoint_status | 0 | 12805 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU050_SetPoint_command | 246 | IU050_SetPoint_command | 1 | 12806 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU050_Room_Temperature | 246 | IU050_Room_Temperature | 0 | 12807 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU050_FanSpeed_status | 246 | IU050_FanSpeed_status | 13 | 12808 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU050_FanSpeed_command | 246 | IU050_FanSpeed_command | 14 | 12809 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU050_AirDirection_status | 246 | IU050_AirDirection_status | 13 | 12810 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU050_AirDirection_command | 246 | IU050_AirDirection_command | 14 | 12811 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU050_FilterSign_status | 246 | IU050_FilterSign_status | 3 | 12812 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU050_FilterSign_Reset_command | 246 | IU050_FilterSign_Reset_command | 4 | 12813 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU050_ErrorCode | 246 | IU050_ErrorCode | 13/0** | 12814 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU050_RemoteControl_Lock | 246 | IU050_RemoteControl_Lock | 19 | 12815 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU050_Occupancy | 246 | IU050_Occupancy | 19 | 12830 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU050_Consumption_Yesterday | 246 | IU050_Consumption_Yesterday | 0 | 12831 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU050_Consumption_Today | 246 | IU050_Consumption_Today | 0 | 12832 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU050_Consumption_Total | 246 | IU050_Consumption_Total | 0 | 12833 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU051_IU_Exist | 246 | IU051_IU_Exist | 3 | 13056 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU051_OnOff_status | 246 | IU051_OnOff_status | 3 | 13057 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU051_OnOff_command | 246 | IU051_OnOff_command | 4 | 13058 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU051_Mode_status | 246 | IU051_Mode_status | 13 | 13059 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU051_Mode_command | 246 | IU051_Mode_command | 14 | 13060 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU051_SetPoint_status | 246 | IU051_SetPoint_status | 0 | 13061 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU051_SetPoint_command | 246 | IU051_SetPoint_command | 1 | 13062 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU051_Room_Temperature | 246 | IU051_Room_Temperature | 0 | 13063 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU051_FanSpeed_status | 246 | IU051_FanSpeed_status | 13 | 13064 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU051_FanSpeed_command | 246 | IU051_FanSpeed_command | 14 | 13065 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU051_AirDirection_status | 246 | IU051_AirDirection_status | 13 | 13066 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU051_AirDirection_command | 246 | IU051_AirDirection_command | 14 | 13067 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU051_FilterSign_status | 246 | IU051_FilterSign_status | 3 | 13068 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU051_FilterSign_Reset_command | 246 | IU051_FilterSign_Reset_command | 4 | 13069 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU051_ErrorCode | 246 | IU051_ErrorCode | 13/0** | 13070 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU051_RemoteControl_Lock | 246 | IU051_RemoteControl_Lock | 19 | 13071 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU051_Occupancy | 246 | IU051_Occupancy | 19 | 13086 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU051_Consumption_Yesterday | 246 | IU051_Consumption_Yesterday | 0 | 13087 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU051_Consumption_Today | 246 | IU051_Consumption_Today | 0 | 13088 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU051_Consumption_Total | 246 | IU051_Consumption_Total | 0 | 13089 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU052_IU_Exist | 246 | IU052_IU_Exist | 3 | 13312 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU052_OnOff_status | 246 | IU052_OnOff_status | 3 | 13313 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU052_OnOff_command | 246 | IU052_OnOff_command | 4 | 13314 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU052_Mode_status | 246 | IU052_Mode_status | 13 | 13315 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU052_Mode_command | 246 | IU052_Mode_command | 14 | 13316 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU052_SetPoint_status | 246 | IU052_SetPoint_status | 0 | 13317 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU052_SetPoint_command | 246 | IU052_SetPoint_command | 1 | 13318 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU052_Room_Temperature | 246 | IU052_Room_Temperature | 0 | 13319 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU052_FanSpeed_status | 246 | IU052_FanSpeed_status | 13 | 13320 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU052_FanSpeed_command | 246 | IU052_FanSpeed_command | 14 | 13321 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU052_AirDirection_status | 246 | IU052_AirDirection_status | 13 | 13322 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU052_AirDirection_command | 246 | IU052_AirDirection_command | 14 | 13323 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU052_FilterSign_status | 246 | IU052_FilterSign_status | 3 | 13324 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU052_FilterSign_Reset_command | 246 | IU052_FilterSign_Reset_command | 4 | 13325 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU052_ErrorCode | 246 | IU052_ErrorCode | 13/0** | 13326 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU052_RemoteControl_Lock | 246 | IU052_RemoteControl_Lock | 19 | 13327 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU052_Occupancy | 246 | IU052_Occupancy | 19 | 13342 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU052_Consumption_Yesterday | 246 | IU052_Consumption_Yesterday | 0 | 13343 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU052_Consumption_Today | 246 | IU052_Consumption_Today | 0 | 13344 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU052_Consumption_Total | 246 | IU052_Consumption_Total | 0 | 13345 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU053_IU_Exist | 246 | IU053_IU_Exist | 3 | 13568 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU053_OnOff_status | 246 | IU053_OnOff_status | 3 | 13569 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU053_OnOff_command | 246 | IU053_OnOff_command | 4 | 13570 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU053_Mode_status | 246 | IU053_Mode_status | 13 | 13571 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU053_Mode_command | 246 | IU053_Mode_command | 14 | 13572 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU053_SetPoint_status | 246 | IU053_SetPoint_status | 0 | 13573 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU053_SetPoint_command | 246 | IU053_SetPoint_command | 1 | 13574 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU053_Room_Temperature | 246 | IU053_Room_Temperature | 0 | 13575 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU053_FanSpeed_status | 246 | IU053_FanSpeed_status | 13 | 13576 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU053_FanSpeed_command | 246 | IU053_FanSpeed_command | 14 | 13577 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU053_AirDirection_status | 246 | IU053_AirDirection_status | 13 | 13578 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU053_AirDirection_command | 246 | IU053_AirDirection_command | 14 | 13579 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU053_FilterSign_status | 246 | IU053_FilterSign_status | 3 | 13580 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU053_FilterSign_Reset_command | 246 | IU053_FilterSign_Reset_command | 4 | 13581 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU053_ErrorCode | 246 | IU053_ErrorCode | 13/0** | 13582 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU053_RemoteControl_Lock | 246 | IU053_RemoteControl_Lock | 19 | 13583 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU053_Occupancy | 246 | IU053_Occupancy | 19 | 13598 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU053_Consumption_Yesterday | 246 | IU053_Consumption_Yesterday | 0 | 13599 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU053_Consumption_Today | 246 | IU053_Consumption_Today | 0 | 13600 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU053_Consumption_Total | 246 | IU053_Consumption_Total | 0 | 13601 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU054_IU_Exist | 246 | IU054_IU_Exist | 3 | 13824 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU054_OnOff_status | 246 | IU054_OnOff_status | 3 | 13825 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU054_OnOff_command | 246 | IU054_OnOff_command | 4 | 13826 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU054_Mode_status | 246 | IU054_Mode_status | 13 | 13827 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU054_Mode_command | 246 | IU054_Mode_command | 14 | 13828 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU054_SetPoint_status | 246 | IU054_SetPoint_status | 0 | 13829 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU054_SetPoint_command | 246 | IU054_SetPoint_command | 1 | 13830 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU054_Room_Temperature | 246 | IU054_Room_Temperature | 0 | 13831 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU054_FanSpeed_status | 246 | IU054_FanSpeed_status | 13 | 13832 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU054_FanSpeed_command | 246 | IU054_FanSpeed_command | 14 | 13833 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU054_AirDirection_status | 246 | IU054_AirDirection_status | 13 | 13834 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU054_AirDirection_command | 246 | IU054_AirDirection_command | 14 | 13835 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU054_FilterSign_status | 246 | IU054_FilterSign_status | 3 | 13836 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU054_FilterSign_Reset_command | 246 | IU054_FilterSign_Reset_command | 4 | 13837 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU054_ErrorCode | 246 | IU054_ErrorCode | 13/0** | 13838 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU054_RemoteControl_Lock | 246 | IU054_RemoteControl_Lock | 19 | 13839 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU054_Occupancy | 246 | IU054_Occupancy | 19 | 13854 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU054_Consumption_Yesterday | 246 | IU054_Consumption_Yesterday | 0 | 13855 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU054_Consumption_Today | 246 | IU054_Consumption_Today | 0 | 13856 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU054_Consumption_Total | 246 | IU054_Consumption_Total | 0 | 13857 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU055_IU_Exist | 246 | IU055_IU_Exist | 3 | 14080 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU055_OnOff_status | 246 | IU055_OnOff_status | 3 | 14081 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU055_OnOff_command | 246 | IU055_OnOff_command | 4 | 14082 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU055_Mode_status | 246 | IU055_Mode_status | 13 | 14083 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU055_Mode_command | 246 | IU055_Mode_command | 14 | 14084 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU055_SetPoint_status | 246 | IU055_SetPoint_status | 0 | 14085 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU055_SetPoint_command | 246 | IU055_SetPoint_command | 1 | 14086 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU055_Room_Temperature | 246 | IU055_Room_Temperature | 0 | 14087 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU055_FanSpeed_status | 246 | IU055_FanSpeed_status | 13 | 14088 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU055_FanSpeed_command | 246 | IU055_FanSpeed_command | 14 | 14089 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU055_AirDirection_status | 246 | IU055_AirDirection_status | 13 | 14090 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU055_AirDirection_command | 246 | IU055_AirDirection_command | 14 | 14091 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU055_FilterSign_status | 246 | IU055_FilterSign_status | 3 | 14092 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU055_FilterSign_Reset_command | 246 | IU055_FilterSign_Reset_command | 4 | 14093 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU055_ErrorCode | 246 | IU055_ErrorCode | 13/0** | 14094 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU055_RemoteControl_Lock | 246 | IU055_RemoteControl_Lock | 19 | 14095 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU055_Occupancy | 246 | IU055_Occupancy | 19 | 14110 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU055_Consumption_Yesterday | 246 | IU055_Consumption_Yesterday | 0 | 14111 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU055_Consumption_Today | 246 | IU055_Consumption_Today | 0 | 14112 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU055_Consumption_Total | 246 | IU055_Consumption_Total | 0 | 14113 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU056_IU_Exist | 246 | IU056_IU_Exist | 3 | 14336 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU056_OnOff_status | 246 | IU056_OnOff_status | 3 | 14337 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU056_OnOff_command | 246 | IU056_OnOff_command | 4 | 14338 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU056_Mode_status | 246 | IU056_Mode_status | 13 | 14339 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU056_Mode_command | 246 | IU056_Mode_command | 14 | 14340 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU056_SetPoint_status | 246 | IU056_SetPoint_status | 0 | 14341 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU056_SetPoint_command | 246 | IU056_SetPoint_command | 1 | 14342 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU056_Room_Temperature | 246 | IU056_Room_Temperature | 0 | 14343 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU056_FanSpeed_status | 246 | IU056_FanSpeed_status | 13 | 14344 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU056_FanSpeed_command | 246 | IU056_FanSpeed_command | 14 | 14345 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU056_AirDirection_status | 246 | IU056_AirDirection_status | 13 | 14346 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU056_AirDirection_command | 246 | IU056_AirDirection_command | 14 | 14347 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU056_FilterSign_status | 246 | IU056_FilterSign_status | 3 | 14348 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU056_FilterSign_Reset_command | 246 | IU056_FilterSign_Reset_command | 4 | 14349 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU056_ErrorCode | 246 | IU056_ErrorCode | 13/0** | 14350 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU056_RemoteControl_Lock | 246 | IU056_RemoteControl_Lock | 19 | 14351 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU056_Occupancy | 246 | IU056_Occupancy | 19 | 14366 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU056_Consumption_Yesterday | 246 | IU056_Consumption_Yesterday | 0 | 14367 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU056_Consumption_Today | 246 | IU056_Consumption_Today | 0 | 14368 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU056_Consumption_Total | 246 | IU056_Consumption_Total | 0 | 14369 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU057_IU_Exist | 246 | IU057_IU_Exist | 3 | 14592 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU057_OnOff_status | 246 | IU057_OnOff_status | 3 | 14593 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU057_OnOff_command | 246 | IU057_OnOff_command | 4 | 14594 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU057_Mode_status | 246 | IU057_Mode_status | 13 | 14595 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU057_Mode_command | 246 | IU057_Mode_command | 14 | 14596 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU057_SetPoint_status | 246 | IU057_SetPoint_status | 0 | 14597 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU057_SetPoint_command | 246 | IU057_SetPoint_command | 1 | 14598 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU057_Room_Temperature | 246 | IU057_Room_Temperature | 0 | 14599 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU057_FanSpeed_status | 246 | IU057_FanSpeed_status | 13 | 14600 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU057_FanSpeed_command | 246 | IU057_FanSpeed_command | 14 | 14601 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU057_AirDirection_status | 246 | IU057_AirDirection_status | 13 | 14602 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU057_AirDirection_command | 246 | IU057_AirDirection_command | 14 | 14603 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU057_FilterSign_status | 246 | IU057_FilterSign_status | 3 | 14604 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU057_FilterSign_Reset_command | 246 | IU057_FilterSign_Reset_command | 4 | 14605 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU057_ErrorCode | 246 | IU057_ErrorCode | 13/0** | 14606 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU057_RemoteControl_Lock | 246 | IU057_RemoteControl_Lock | 19 | 14607 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU057_Occupancy | 246 | IU057_Occupancy | 19 | 14622 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU057_Consumption_Yesterday | 246 | IU057_Consumption_Yesterday | 0 | 14623 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU057_Consumption_Today | 246 | IU057_Consumption_Today | 0 | 14624 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU057_Consumption_Total | 246 | IU057_Consumption_Total | 0 | 14625 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU058_IU_Exist | 246 | IU058_IU_Exist | 3 | 14848 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU058_OnOff_status | 246 | IU058_OnOff_status | 3 | 14849 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU058_OnOff_command | 246 | IU058_OnOff_command | 4 | 14850 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU058_Mode_status | 246 | IU058_Mode_status | 13 | 14851 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU058_Mode_command | 246 | IU058_Mode_command | 14 | 14852 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU058_SetPoint_status | 246 | IU058_SetPoint_status | 0 | 14853 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU058_SetPoint_command | 246 | IU058_SetPoint_command | 1 | 14854 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU058_Room_Temperature | 246 | IU058_Room_Temperature | 0 | 14855 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU058_FanSpeed_status | 246 | IU058_FanSpeed_status | 13 | 14856 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU058_FanSpeed_command | 246 | IU058_FanSpeed_command | 14 | 14857 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU058_AirDirection_status | 246 | IU058_AirDirection_status | 13 | 14858 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU058_AirDirection_command | 246 | IU058_AirDirection_command | 14 | 14859 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU058_FilterSign_status | 246 | IU058_FilterSign_status | 3 | 14860 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU058_FilterSign_Reset_command | 246 | IU058_FilterSign_Reset_command | 4 | 14861 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU058_ErrorCode | 246 | IU058_ErrorCode | 13/0** | 14862 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU058_RemoteControl_Lock | 246 | IU058_RemoteControl_Lock | 19 | 14863 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU058_Occupancy | 246 | IU058_Occupancy | 19 | 14878 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU058_Consumption_Yesterday | 246 | IU058_Consumption_Yesterday | 0 | 14879 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU058_Consumption_Today | 246 | IU058_Consumption_Today | 0 | 14880 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU058_Consumption_Total | 246 | IU058_Consumption_Total | 0 | 14881 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU059_IU_Exist | 246 | IU059_IU_Exist | 3 | 15104 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU059_OnOff_status | 246 | IU059_OnOff_status | 3 | 15105 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU059_OnOff_command | 246 | IU059_OnOff_command | 4 | 15106 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU059_Mode_status | 246 | IU059_Mode_status | 13 | 15107 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU059_Mode_command | 246 | IU059_Mode_command | 14 | 15108 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU059_SetPoint_status | 246 | IU059_SetPoint_status | 0 | 15109 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU059_SetPoint_command | 246 | IU059_SetPoint_command | 1 | 15110 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU059_Room_Temperature | 246 | IU059_Room_Temperature | 0 | 15111 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU059_FanSpeed_status | 246 | IU059_FanSpeed_status | 13 | 15112 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU059_FanSpeed_command | 246 | IU059_FanSpeed_command | 14 | 15113 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU059_AirDirection_status | 246 | IU059_AirDirection_status | 13 | 15114 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU059_AirDirection_command | 246 | IU059_AirDirection_command | 14 | 15115 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU059_FilterSign_status | 246 | IU059_FilterSign_status | 3 | 15116 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU059_FilterSign_Reset_command | 246 | IU059_FilterSign_Reset_command | 4 | 15117 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU059_ErrorCode | 246 | IU059_ErrorCode | 13/0** | 15118 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU059_RemoteControl_Lock | 246 | IU059_RemoteControl_Lock | 19 | 15119 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU059_Occupancy | 246 | IU059_Occupancy | 19 | 15134 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU059_Consumption_Yesterday | 246 | IU059_Consumption_Yesterday | 0 | 15135 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU059_Consumption_Today | 246 | IU059_Consumption_Today | 0 | 15136 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU059_Consumption_Total | 246 | IU059_Consumption_Total | 0 | 15137 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU060_IU_Exist | 246 | IU060_IU_Exist | 3 | 15360 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU060_OnOff_status | 246 | IU060_OnOff_status | 3 | 15361 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU060_OnOff_command | 246 | IU060_OnOff_command | 4 | 15362 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU060_Mode_status | 246 | IU060_Mode_status | 13 | 15363 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU060_Mode_command | 246 | IU060_Mode_command | 14 | 15364 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU060_SetPoint_status | 246 | IU060_SetPoint_status | 0 | 15365 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU060_SetPoint_command | 246 | IU060_SetPoint_command | 1 | 15366 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU060_Room_Temperature | 246 | IU060_Room_Temperature | 0 | 15367 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU060_FanSpeed_status | 246 | IU060_FanSpeed_status | 13 | 15368 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU060_FanSpeed_command | 246 | IU060_FanSpeed_command | 14 | 15369 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU060_AirDirection_status | 246 | IU060_AirDirection_status | 13 | 15370 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU060_AirDirection_command | 246 | IU060_AirDirection_command | 14 | 15371 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU060_FilterSign_status | 246 | IU060_FilterSign_status | 3 | 15372 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU060_FilterSign_Reset_command | 246 | IU060_FilterSign_Reset_command | 4 | 15373 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU060_ErrorCode | 246 | IU060_ErrorCode | 13/0** | 15374 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU060_RemoteControl_Lock | 246 | IU060_RemoteControl_Lock | 19 | 15375 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU060_Occupancy | 246 | IU060_Occupancy | 19 | 15390 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU060_Consumption_Yesterday | 246 | IU060_Consumption_Yesterday | 0 | 15391 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU060_Consumption_Today | 246 | IU060_Consumption_Today | 0 | 15392 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU060_Consumption_Total | 246 | IU060_Consumption_Total | 0 | 15393 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU061_IU_Exist | 246 | IU061_IU_Exist | 3 | 15616 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU061_OnOff_status | 246 | IU061_OnOff_status | 3 | 15617 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU061_OnOff_command | 246 | IU061_OnOff_command | 4 | 15618 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU061_Mode_status | 246 | IU061_Mode_status | 13 | 15619 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU061_Mode_command | 246 | IU061_Mode_command | 14 | 15620 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU061_SetPoint_status | 246 | IU061_SetPoint_status | 0 | 15621 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU061_SetPoint_command | 246 | IU061_SetPoint_command | 1 | 15622 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU061_Room_Temperature | 246 | IU061_Room_Temperature | 0 | 15623 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU061_FanSpeed_status | 246 | IU061_FanSpeed_status | 13 | 15624 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU061_FanSpeed_command | 246 | IU061_FanSpeed_command | 14 | 15625 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU061_AirDirection_status | 246 | IU061_AirDirection_status | 13 | 15626 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU061_AirDirection_command | 246 | IU061_AirDirection_command | 14 | 15627 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU061_FilterSign_status | 246 | IU061_FilterSign_status | 3 | 15628 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU061_FilterSign_Reset_command | 246 | IU061_FilterSign_Reset_command | 4 | 15629 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU061_ErrorCode | 246 | IU061_ErrorCode | 13/0** | 15630 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU061_RemoteControl_Lock | 246 | IU061_RemoteControl_Lock | 19 | 15631 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU061_Occupancy | 246 | IU061_Occupancy | 19 | 15646 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU061_Consumption_Yesterday | 246 | IU061_Consumption_Yesterday | 0 | 15647 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU061_Consumption_Today | 246 | IU061_Consumption_Today | 0 | 15648 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU061_Consumption_Total | 246 | IU061_Consumption_Total | 0 | 15649 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU062_IU_Exist | 246 | IU062_IU_Exist | 3 | 15872 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU062_OnOff_status | 246 | IU062_OnOff_status | 3 | 15873 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU062_OnOff_command | 246 | IU062_OnOff_command | 4 | 15874 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU062_Mode_status | 246 | IU062_Mode_status | 13 | 15875 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU062_Mode_command | 246 | IU062_Mode_command | 14 | 15876 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU062_SetPoint_status | 246 | IU062_SetPoint_status | 0 | 15877 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU062_SetPoint_command | 246 | IU062_SetPoint_command | 1 | 15878 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU062_Room_Temperature | 246 | IU062_Room_Temperature | 0 | 15879 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU062_FanSpeed_status | 246 | IU062_FanSpeed_status | 13 | 15880 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU062_FanSpeed_command | 246 | IU062_FanSpeed_command | 14 | 15881 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU062_AirDirection_status | 246 | IU062_AirDirection_status | 13 | 15882 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU062_AirDirection_command | 246 | IU062_AirDirection_command | 14 | 15883 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU062_FilterSign_status | 246 | IU062_FilterSign_status | 3 | 15884 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU062_FilterSign_Reset_command | 246 | IU062_FilterSign_Reset_command | 4 | 15885 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU062_ErrorCode | 246 | IU062_ErrorCode | 13/0** | 15886 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU062_RemoteControl_Lock | 246 | IU062_RemoteControl_Lock | 19 | 15887 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU062_Occupancy | 246 | IU062_Occupancy | 19 | 15902 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU062_Consumption_Yesterday | 246 | IU062_Consumption_Yesterday | 0 | 15903 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU062_Consumption_Today | 246 | IU062_Consumption_Today | 0 | 15904 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU062_Consumption_Total | 246 | IU062_Consumption_Total | 0 | 15905 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU063_IU_Exist | 246 | IU063_IU_Exist | 3 | 16128 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU063_OnOff_status | 246 | IU063_OnOff_status | 3 | 16129 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU063_OnOff_command | 246 | IU063_OnOff_command | 4 | 16130 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU063_Mode_status | 246 | IU063_Mode_status | 13 | 16131 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU063_Mode_command | 246 | IU063_Mode_command | 14 | 16132 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU063_SetPoint_status | 246 | IU063_SetPoint_status | 0 | 16133 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU063_SetPoint_command | 246 | IU063_SetPoint_command | 1 | 16134 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU063_Room_Temperature | 246 | IU063_Room_Temperature | 0 | 16135 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU063_FanSpeed_status | 246 | IU063_FanSpeed_status | 13 | 16136 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU063_FanSpeed_command | 246 | IU063_FanSpeed_command | 14 | 16137 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU063_AirDirection_status | 246 | IU063_AirDirection_status | 13 | 16138 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU063_AirDirection_command | 246 | IU063_AirDirection_command | 14 | 16139 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU063_FilterSign_status | 246 | IU063_FilterSign_status | 3 | 16140 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU063_FilterSign_Reset_command | 246 | IU063_FilterSign_Reset_command | 4 | 16141 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU063_ErrorCode | 246 | IU063_ErrorCode | 13/0** | 16142 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU063_RemoteControl_Lock | 246 | IU063_RemoteControl_Lock | 19 | 16143 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU063_Occupancy | 246 | IU063_Occupancy | 19 | 16158 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU063_Consumption_Yesterday | 246 | IU063_Consumption_Yesterday | 0 | 16159 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU063_Consumption_Today | 246 | IU063_Consumption_Today | 0 | 16160 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU063_Consumption_Total | 246 | IU063_Consumption_Total | 0 | 16161 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU064_IU_Exist | 246 | IU064_IU_Exist | 3 | 16384 | 1-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU064_OnOff_status | 246 | IU064_OnOff_status | 3 | 16385 | 1-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU064_OnOff_command | 246 | IU064_OnOff_command | 4 | 16386 | 1-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU064_Mode_status | 246 | IU064_Mode_status | 13 | 16387 | 1-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU064_Mode_command | 246 | IU064_Mode_command | 14 | 16388 | 1-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU064_SetPoint_status | 246 | IU064_SetPoint_status | 0 | 16389 | 1-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU064_SetPoint_command | 246 | IU064_SetPoint_command | 1 | 16390 | 1-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU064_Room_Temperature | 246 | IU064_Room_Temperature | 0 | 16391 | 1-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU064_FanSpeed_status | 246 | IU064_FanSpeed_status | 13 | 16392 | 1-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU064_FanSpeed_command | 246 | IU064_FanSpeed_command | 14 | 16393 | 1-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU064_AirDirection_status | 246 | IU064_AirDirection_status | 13 | 16394 | 1-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU064_AirDirection_command | 246 | IU064_AirDirection_command | 14 | 16395 | 1-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU064_FilterSign_status | 246 | IU064_FilterSign_status | 3 | 16396 | 1-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU064_FilterSign_Reset_command | 246 | IU064_FilterSign_Reset_command | 4 | 16397 | 1-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU064_ErrorCode | 246 | IU064_ErrorCode | 13/0** | 16398 | 1-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU064_RemoteControl_Lock | 246 | IU064_RemoteControl_Lock | 19 | 16399 | 1-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU064_Occupancy | 246 | IU064_Occupancy | 19 | 16414 | 1-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU064_Consumption_Yesterday | 246 | IU064_Consumption_Yesterday | 0 | 16415 | 1-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU064_Consumption_Today | 246 | IU064_Consumption_Today | 0 | 16416 | 1-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU064_Consumption_Total | 246 | IU064_Consumption_Total | 0 | 16417 | 1-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU065_IU_Exist | 246 | IU065_IU_Exist | 3 | 16640 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU065_OnOff_status | 246 | IU065_OnOff_status | 3 | 16641 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU065_OnOff_command | 246 | IU065_OnOff_command | 4 | 16642 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU065_Mode_status | 246 | IU065_Mode_status | 13 | 16643 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU065_Mode_command | 246 | IU065_Mode_command | 14 | 16644 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU065_SetPoint_status | 246 | IU065_SetPoint_status | 0 | 16645 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU065_SetPoint_command | 246 | IU065_SetPoint_command | 1 | 16646 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU065_Room_Temperature | 246 | IU065_Room_Temperature | 0 | 16647 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU065_FanSpeed_status | 246 | IU065_FanSpeed_status | 13 | 16648 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU065_FanSpeed_command | 246 | IU065_FanSpeed_command | 14 | 16649 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU065_AirDirection_status | 246 | IU065_AirDirection_status | 13 | 16650 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU065_AirDirection_command | 246 | IU065_AirDirection_command | 14 | 16651 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU065_FilterSign_status | 246 | IU065_FilterSign_status | 3 | 16652 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU065_FilterSign_Reset_command | 246 | IU065_FilterSign_Reset_command | 4 | 16653 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU065_ErrorCode | 246 | IU065_ErrorCode | 13/0** | 16654 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU065_RemoteControl_Lock | 246 | IU065_RemoteControl_Lock | 19 | 16655 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU065_Occupancy | 246 | IU065_Occupancy | 19 | 16670 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU065_Consumption_Yesterday | 246 | IU065_Consumption_Yesterday | 0 | 16671 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU065_Consumption_Today | 246 | IU065_Consumption_Today | 0 | 16672 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU065_Consumption_Total | 246 | IU065_Consumption_Total | 0 | 16673 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU066_IU_Exist | 246 | IU066_IU_Exist | 3 | 16896 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU066_OnOff_status | 246 | IU066_OnOff_status | 3 | 16897 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU066_OnOff_command | 246 | IU066_OnOff_command | 4 | 16898 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU066_Mode_status | 246 | IU066_Mode_status | 13 | 16899 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU066_Mode_command | 246 | IU066_Mode_command | 14 | 16900 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU066_SetPoint_status | 246 | IU066_SetPoint_status | 0 | 16901 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU066_SetPoint_command | 246 | IU066_SetPoint_command | 1 | 16902 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU066_Room_Temperature | 246 | IU066_Room_Temperature | 0 | 16903 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU066_FanSpeed_status | 246 | IU066_FanSpeed_status | 13 | 16904 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU066_FanSpeed_command | 246 | IU066_FanSpeed_command | 14 | 16905 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU066_AirDirection_status | 246 | IU066_AirDirection_status | 13 | 16906 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU066_AirDirection_command | 246 | IU066_AirDirection_command | 14 | 16907 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU066_FilterSign_status | 246 | IU066_FilterSign_status | 3 | 16908 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU066_FilterSign_Reset_command | 246 | IU066_FilterSign_Reset_command | 4 | 16909 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU066_ErrorCode | 246 | IU066_ErrorCode | 13/0** | 16910 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU066_RemoteControl_Lock | 246 | IU066_RemoteControl_Lock | 19 | 16911 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU066_Occupancy | 246 | IU066_Occupancy | 19 | 16926 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU066_Consumption_Yesterday | 246 | IU066_Consumption_Yesterday | 0 | 16927 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU066_Consumption_Today | 246 | IU066_Consumption_Today | 0 | 16928 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU066_Consumption_Total | 246 | IU066_Consumption_Total | 0 | 16929 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU067_IU_Exist | 246 | IU067_IU_Exist | 3 | 17152 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU067_OnOff_status | 246 | IU067_OnOff_status | 3 | 17153 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU067_OnOff_command | 246 | IU067_OnOff_command | 4 | 17154 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU067_Mode_status | 246 | IU067_Mode_status | 13 | 17155 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU067_Mode_command | 246 | IU067_Mode_command | 14 | 17156 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU067_SetPoint_status | 246 | IU067_SetPoint_status | 0 | 17157 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU067_SetPoint_command | 246 | IU067_SetPoint_command | 1 | 17158 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU067_Room_Temperature | 246 | IU067_Room_Temperature | 0 | 17159 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU067_FanSpeed_status | 246 | IU067_FanSpeed_status | 13 | 17160 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU067_FanSpeed_command | 246 | IU067_FanSpeed_command | 14 | 17161 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU067_AirDirection_status | 246 | IU067_AirDirection_status | 13 | 17162 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU067_AirDirection_command | 246 | IU067_AirDirection_command | 14 | 17163 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU067_FilterSign_status | 246 | IU067_FilterSign_status | 3 | 17164 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU067_FilterSign_Reset_command | 246 | IU067_FilterSign_Reset_command | 4 | 17165 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU067_ErrorCode | 246 | IU067_ErrorCode | 13/0** | 17166 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU067_RemoteControl_Lock | 246 | IU067_RemoteControl_Lock | 19 | 17167 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU067_Occupancy | 246 | IU067_Occupancy | 19 | 17182 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU067_Consumption_Yesterday | 246 | IU067_Consumption_Yesterday | 0 | 17183 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU067_Consumption_Today | 246 | IU067_Consumption_Today | 0 | 17184 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU067_Consumption_Total | 246 | IU067_Consumption_Total | 0 | 17185 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU068_IU_Exist | 246 | IU068_IU_Exist | 3 | 17408 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU068_OnOff_status | 246 | IU068_OnOff_status | 3 | 17409 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU068_OnOff_command | 246 | IU068_OnOff_command | 4 | 17410 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU068_Mode_status | 246 | IU068_Mode_status | 13 | 17411 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU068_Mode_command | 246 | IU068_Mode_command | 14 | 17412 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU068_SetPoint_status | 246 | IU068_SetPoint_status | 0 | 17413 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU068_SetPoint_command | 246 | IU068_SetPoint_command | 1 | 17414 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU068_Room_Temperature | 246 | IU068_Room_Temperature | 0 | 17415 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU068_FanSpeed_status | 246 | IU068_FanSpeed_status | 13 | 17416 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU068_FanSpeed_command | 246 | IU068_FanSpeed_command | 14 | 17417 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU068_AirDirection_status | 246 | IU068_AirDirection_status | 13 | 17418 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU068_AirDirection_command | 246 | IU068_AirDirection_command | 14 | 17419 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU068_FilterSign_status | 246 | IU068_FilterSign_status | 3 | 17420 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU068_FilterSign_Reset_command | 246 | IU068_FilterSign_Reset_command | 4 | 17421 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU068_ErrorCode | 246 | IU068_ErrorCode | 13/0** | 17422 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU068_RemoteControl_Lock | 246 | IU068_RemoteControl_Lock | 19 | 17423 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU068_Occupancy | 246 | IU068_Occupancy | 19 | 17438 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU068_Consumption_Yesterday | 246 | IU068_Consumption_Yesterday | 0 | 17439 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU068_Consumption_Today | 246 | IU068_Consumption_Today | 0 | 17440 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU068_Consumption_Total | 246 | IU068_Consumption_Total | 0 | 17441 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU069_IU_Exist | 246 | IU069_IU_Exist | 3 | 17664 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU069_OnOff_status | 246 | IU069_OnOff_status | 3 | 17665 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU069_OnOff_command | 246 | IU069_OnOff_command | 4 | 17666 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU069_Mode_status | 246 | IU069_Mode_status | 13 | 17667 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU069_Mode_command | 246 | IU069_Mode_command | 14 | 17668 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU069_SetPoint_status | 246 | IU069_SetPoint_status | 0 | 17669 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU069_SetPoint_command | 246 | IU069_SetPoint_command | 1 | 17670 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU069_Room_Temperature | 246 | IU069_Room_Temperature | 0 | 17671 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU069_FanSpeed_status | 246 | IU069_FanSpeed_status | 13 | 17672 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU069_FanSpeed_command | 246 | IU069_FanSpeed_command | 14 | 17673 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU069_AirDirection_status | 246 | IU069_AirDirection_status | 13 | 17674 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU069_AirDirection_command | 246 | IU069_AirDirection_command | 14 | 17675 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU069_FilterSign_status | 246 | IU069_FilterSign_status | 3 | 17676 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU069_FilterSign_Reset_command | 246 | IU069_FilterSign_Reset_command | 4 | 17677 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU069_ErrorCode | 246 | IU069_ErrorCode | 13/0** | 17678 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU069_RemoteControl_Lock | 246 | IU069_RemoteControl_Lock | 19 | 17679 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU069_Occupancy | 246 | IU069_Occupancy | 19 | 17694 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU069_Consumption_Yesterday | 246 | IU069_Consumption_Yesterday | 0 | 17695 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU069_Consumption_Today | 246 | IU069_Consumption_Today | 0 | 17696 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU069_Consumption_Total | 246 | IU069_Consumption_Total | 0 | 17697 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU070_IU_Exist | 246 | IU070_IU_Exist | 3 | 17920 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU070_OnOff_status | 246 | IU070_OnOff_status | 3 | 17921 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU070_OnOff_command | 246 | IU070_OnOff_command | 4 | 17922 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU070_Mode_status | 246 | IU070_Mode_status | 13 | 17923 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU070_Mode_command | 246 | IU070_Mode_command | 14 | 17924 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU070_SetPoint_status | 246 | IU070_SetPoint_status | 0 | 17925 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU070_SetPoint_command | 246 | IU070_SetPoint_command | 1 | 17926 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU070_Room_Temperature | 246 | IU070_Room_Temperature | 0 | 17927 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU070_FanSpeed_status | 246 | IU070_FanSpeed_status | 13 | 17928 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU070_FanSpeed_command | 246 | IU070_FanSpeed_command | 14 | 17929 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU070_AirDirection_status | 246 | IU070_AirDirection_status | 13 | 17930 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU070_AirDirection_command | 246 | IU070_AirDirection_command | 14 | 17931 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU070_FilterSign_status | 246 | IU070_FilterSign_status | 3 | 17932 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU070_FilterSign_Reset_command | 246 | IU070_FilterSign_Reset_command | 4 | 17933 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU070_ErrorCode | 246 | IU070_ErrorCode | 13/0** | 17934 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU070_RemoteControl_Lock | 246 | IU070_RemoteControl_Lock | 19 | 17935 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU070_Occupancy | 246 | IU070_Occupancy | 19 | 17950 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU070_Consumption_Yesterday | 246 | IU070_Consumption_Yesterday | 0 | 17951 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU070_Consumption_Today | 246 | IU070_Consumption_Today | 0 | 17952 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU070_Consumption_Total | 246 | IU070_Consumption_Total | 0 | 17953 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU071_IU_Exist | 246 | IU071_IU_Exist | 3 | 18176 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU071_OnOff_status | 246 | IU071_OnOff_status | 3 | 18177 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU071_OnOff_command | 246 | IU071_OnOff_command | 4 | 18178 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU071_Mode_status | 246 | IU071_Mode_status | 13 | 18179 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU071_Mode_command | 246 | IU071_Mode_command | 14 | 18180 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU071_SetPoint_status | 246 | IU071_SetPoint_status | 0 | 18181 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU071_SetPoint_command | 246 | IU071_SetPoint_command | 1 | 18182 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU071_Room_Temperature | 246 | IU071_Room_Temperature | 0 | 18183 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU071_FanSpeed_status | 246 | IU071_FanSpeed_status | 13 | 18184 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU071_FanSpeed_command | 246 | IU071_FanSpeed_command | 14 | 18185 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU071_AirDirection_status | 246 | IU071_AirDirection_status | 13 | 18186 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU071_AirDirection_command | 246 | IU071_AirDirection_command | 14 | 18187 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU071_FilterSign_status | 246 | IU071_FilterSign_status | 3 | 18188 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU071_FilterSign_Reset_command | 246 | IU071_FilterSign_Reset_command | 4 | 18189 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU071_ErrorCode | 246 | IU071_ErrorCode | 13/0** | 18190 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU071_RemoteControl_Lock | 246 | IU071_RemoteControl_Lock | 19 | 18191 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU071_Occupancy | 246 | IU071_Occupancy | 19 | 18206 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU071_Consumption_Yesterday | 246 | IU071_Consumption_Yesterday | 0 | 18207 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU071_Consumption_Today | 246 | IU071_Consumption_Today | 0 | 18208 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU071_Consumption_Total | 246 | IU071_Consumption_Total | 0 | 18209 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU072_IU_Exist | 246 | IU072_IU_Exist | 3 | 18432 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU072_OnOff_status | 246 | IU072_OnOff_status | 3 | 18433 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU072_OnOff_command | 246 | IU072_OnOff_command | 4 | 18434 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU072_Mode_status | 246 | IU072_Mode_status | 13 | 18435 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU072_Mode_command | 246 | IU072_Mode_command | 14 | 18436 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU072_SetPoint_status | 246 | IU072_SetPoint_status | 0 | 18437 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU072_SetPoint_command | 246 | IU072_SetPoint_command | 1 | 18438 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU072_Room_Temperature | 246 | IU072_Room_Temperature | 0 | 18439 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU072_FanSpeed_status | 246 | IU072_FanSpeed_status | 13 | 18440 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU072_FanSpeed_command | 246 | IU072_FanSpeed_command | 14 | 18441 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU072_AirDirection_status | 246 | IU072_AirDirection_status | 13 | 18442 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU072_AirDirection_command | 246 | IU072_AirDirection_command | 14 | 18443 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU072_FilterSign_status | 246 | IU072_FilterSign_status | 3 | 18444 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU072_FilterSign_Reset_command | 246 | IU072_FilterSign_Reset_command | 4 | 18445 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU072_ErrorCode | 246 | IU072_ErrorCode | 13/0** | 18446 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU072_RemoteControl_Lock | 246 | IU072_RemoteControl_Lock | 19 | 18447 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU072_Occupancy | 246 | IU072_Occupancy | 19 | 18462 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU072_Consumption_Yesterday | 246 | IU072_Consumption_Yesterday | 0 | 18463 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU072_Consumption_Today | 246 | IU072_Consumption_Today | 0 | 18464 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU072_Consumption_Total | 246 | IU072_Consumption_Total | 0 | 18465 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU073_IU_Exist | 246 | IU073_IU_Exist | 3 | 18688 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU073_OnOff_status | 246 | IU073_OnOff_status | 3 | 18689 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU073_OnOff_command | 246 | IU073_OnOff_command | 4 | 18690 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU073_Mode_status | 246 | IU073_Mode_status | 13 | 18691 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU073_Mode_command | 246 | IU073_Mode_command | 14 | 18692 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU073_SetPoint_status | 246 | IU073_SetPoint_status | 0 | 18693 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU073_SetPoint_command | 246 | IU073_SetPoint_command | 1 | 18694 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU073_Room_Temperature | 246 | IU073_Room_Temperature | 0 | 18695 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU073_FanSpeed_status | 246 | IU073_FanSpeed_status | 13 | 18696 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU073_FanSpeed_command | 246 | IU073_FanSpeed_command | 14 | 18697 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU073_AirDirection_status | 246 | IU073_AirDirection_status | 13 | 18698 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU073_AirDirection_command | 246 | IU073_AirDirection_command | 14 | 18699 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU073_FilterSign_status | 246 | IU073_FilterSign_status | 3 | 18700 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU073_FilterSign_Reset_command | 246 | IU073_FilterSign_Reset_command | 4 | 18701 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU073_ErrorCode | 246 | IU073_ErrorCode | 13/0** | 18702 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU073_RemoteControl_Lock | 246 | IU073_RemoteControl_Lock | 19 | 18703 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU073_Occupancy | 246 | IU073_Occupancy | 19 | 18718 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU073_Consumption_Yesterday | 246 | IU073_Consumption_Yesterday | 0 | 18719 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU073_Consumption_Today | 246 | IU073_Consumption_Today | 0 | 18720 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU073_Consumption_Total | 246 | IU073_Consumption_Total | 0 | 18721 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU074_IU_Exist | 246 | IU074_IU_Exist | 3 | 18944 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU074_OnOff_status | 246 | IU074_OnOff_status | 3 | 18945 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU074_OnOff_command | 246 | IU074_OnOff_command | 4 | 18946 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU074_Mode_status | 246 | IU074_Mode_status | 13 | 18947 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU074_Mode_command | 246 | IU074_Mode_command | 14 | 18948 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU074_SetPoint_status | 246 | IU074_SetPoint_status | 0 | 18949 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU074_SetPoint_command | 246 | IU074_SetPoint_command | 1 | 18950 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU074_Room_Temperature | 246 | IU074_Room_Temperature | 0 | 18951 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU074_FanSpeed_status | 246 | IU074_FanSpeed_status | 13 | 18952 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU074_FanSpeed_command | 246 | IU074_FanSpeed_command | 14 | 18953 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU074_AirDirection_status | 246 | IU074_AirDirection_status | 13 | 18954 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU074_AirDirection_command | 246 | IU074_AirDirection_command | 14 | 18955 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU074_FilterSign_status | 246 | IU074_FilterSign_status | 3 | 18956 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU074_FilterSign_Reset_command | 246 | IU074_FilterSign_Reset_command | 4 | 18957 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU074_ErrorCode | 246 | IU074_ErrorCode | 13/0** | 18958 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU074_RemoteControl_Lock | 246 | IU074_RemoteControl_Lock | 19 | 18959 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU074_Occupancy | 246 | IU074_Occupancy | 19 | 18974 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU074_Consumption_Yesterday | 246 | IU074_Consumption_Yesterday | 0 | 18975 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU074_Consumption_Today | 246 | IU074_Consumption_Today | 0 | 18976 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU074_Consumption_Total | 246 | IU074_Consumption_Total | 0 | 18977 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU075_IU_Exist | 246 | IU075_IU_Exist | 3 | 19200 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU075_OnOff_status | 246 | IU075_OnOff_status | 3 | 19201 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU075_OnOff_command | 246 | IU075_OnOff_command | 4 | 19202 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU075_Mode_status | 246 | IU075_Mode_status | 13 | 19203 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU075_Mode_command | 246 | IU075_Mode_command | 14 | 19204 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU075_SetPoint_status | 246 | IU075_SetPoint_status | 0 | 19205 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU075_SetPoint_command | 246 | IU075_SetPoint_command | 1 | 19206 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU075_Room_Temperature | 246 | IU075_Room_Temperature | 0 | 19207 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU075_FanSpeed_status | 246 | IU075_FanSpeed_status | 13 | 19208 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU075_FanSpeed_command | 246 | IU075_FanSpeed_command | 14 | 19209 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU075_AirDirection_status | 246 | IU075_AirDirection_status | 13 | 19210 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU075_AirDirection_command | 246 | IU075_AirDirection_command | 14 | 19211 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU075_FilterSign_status | 246 | IU075_FilterSign_status | 3 | 19212 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU075_FilterSign_Reset_command | 246 | IU075_FilterSign_Reset_command | 4 | 19213 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU075_ErrorCode | 246 | IU075_ErrorCode | 13/0** | 19214 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU075_RemoteControl_Lock | 246 | IU075_RemoteControl_Lock | 19 | 19215 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU075_Occupancy | 246 | IU075_Occupancy | 19 | 19230 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU075_Consumption_Yesterday | 246 | IU075_Consumption_Yesterday | 0 | 19231 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU075_Consumption_Today | 246 | IU075_Consumption_Today | 0 | 19232 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU075_Consumption_Total | 246 | IU075_Consumption_Total | 0 | 19233 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU076_IU_Exist | 246 | IU076_IU_Exist | 3 | 19456 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU076_OnOff_status | 246 | IU076_OnOff_status | 3 | 19457 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU076_OnOff_command | 246 | IU076_OnOff_command | 4 | 19458 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU076_Mode_status | 246 | IU076_Mode_status | 13 | 19459 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU076_Mode_command | 246 | IU076_Mode_command | 14 | 19460 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU076_SetPoint_status | 246 | IU076_SetPoint_status | 0 | 19461 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU076_SetPoint_command | 246 | IU076_SetPoint_command | 1 | 19462 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU076_Room_Temperature | 246 | IU076_Room_Temperature | 0 | 19463 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU076_FanSpeed_status | 246 | IU076_FanSpeed_status | 13 | 19464 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU076_FanSpeed_command | 246 | IU076_FanSpeed_command | 14 | 19465 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU076_AirDirection_status | 246 | IU076_AirDirection_status | 13 | 19466 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU076_AirDirection_command | 246 | IU076_AirDirection_command | 14 | 19467 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU076_FilterSign_status | 246 | IU076_FilterSign_status | 3 | 19468 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU076_FilterSign_Reset_command | 246 | IU076_FilterSign_Reset_command | 4 | 19469 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU076_ErrorCode | 246 | IU076_ErrorCode | 13/0** | 19470 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU076_RemoteControl_Lock | 246 | IU076_RemoteControl_Lock | 19 | 19471 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU076_Occupancy | 246 | IU076_Occupancy | 19 | 19486 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU076_Consumption_Yesterday | 246 | IU076_Consumption_Yesterday | 0 | 19487 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU076_Consumption_Today | 246 | IU076_Consumption_Today | 0 | 19488 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU076_Consumption_Total | 246 | IU076_Consumption_Total | 0 | 19489 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU077_IU_Exist | 246 | IU077_IU_Exist | 3 | 19712 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU077_OnOff_status | 246 | IU077_OnOff_status | 3 | 19713 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU077_OnOff_command | 246 | IU077_OnOff_command | 4 | 19714 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU077_Mode_status | 246 | IU077_Mode_status | 13 | 19715 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU077_Mode_command | 246 | IU077_Mode_command | 14 | 19716 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU077_SetPoint_status | 246 | IU077_SetPoint_status | 0 | 19717 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU077_SetPoint_command | 246 | IU077_SetPoint_command | 1 | 19718 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU077_Room_Temperature | 246 | IU077_Room_Temperature | 0 | 19719 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU077_FanSpeed_status | 246 | IU077_FanSpeed_status | 13 | 19720 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU077_FanSpeed_command | 246 | IU077_FanSpeed_command | 14 | 19721 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU077_AirDirection_status | 246 | IU077_AirDirection_status | 13 | 19722 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU077_AirDirection_command | 246 | IU077_AirDirection_command | 14 | 19723 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU077_FilterSign_status | 246 | IU077_FilterSign_status | 3 | 19724 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU077_FilterSign_Reset_command | 246 | IU077_FilterSign_Reset_command | 4 | 19725 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU077_ErrorCode | 246 | IU077_ErrorCode | 13/0** | 19726 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU077_RemoteControl_Lock | 246 | IU077_RemoteControl_Lock | 19 | 19727 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU077_Occupancy | 246 | IU077_Occupancy | 19 | 19742 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU077_Consumption_Yesterday | 246 | IU077_Consumption_Yesterday | 0 | 19743 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU077_Consumption_Today | 246 | IU077_Consumption_Today | 0 | 19744 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU077_Consumption_Total | 246 | IU077_Consumption_Total | 0 | 19745 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU078_IU_Exist | 246 | IU078_IU_Exist | 3 | 19968 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU078_OnOff_status | 246 | IU078_OnOff_status | 3 | 19969 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU078_OnOff_command | 246 | IU078_OnOff_command | 4 | 19970 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU078_Mode_status | 246 | IU078_Mode_status | 13 | 19971 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU078_Mode_command | 246 | IU078_Mode_command | 14 | 19972 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU078_SetPoint_status | 246 | IU078_SetPoint_status | 0 | 19973 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU078_SetPoint_command | 246 | IU078_SetPoint_command | 1 | 19974 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU078_Room_Temperature | 246 | IU078_Room_Temperature | 0 | 19975 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU078_FanSpeed_status | 246 | IU078_FanSpeed_status | 13 | 19976 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU078_FanSpeed_command | 246 | IU078_FanSpeed_command | 14 | 19977 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU078_AirDirection_status | 246 | IU078_AirDirection_status | 13 | 19978 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU078_AirDirection_command | 246 | IU078_AirDirection_command | 14 | 19979 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU078_FilterSign_status | 246 | IU078_FilterSign_status | 3 | 19980 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU078_FilterSign_Reset_command | 246 | IU078_FilterSign_Reset_command | 4 | 19981 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU078_ErrorCode | 246 | IU078_ErrorCode | 13/0** | 19982 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU078_RemoteControl_Lock | 246 | IU078_RemoteControl_Lock | 19 | 19983 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU078_Occupancy | 246 | IU078_Occupancy | 19 | 19998 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU078_Consumption_Yesterday | 246 | IU078_Consumption_Yesterday | 0 | 19999 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU078_Consumption_Today | 246 | IU078_Consumption_Today | 0 | 20000 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU078_Consumption_Total | 246 | IU078_Consumption_Total | 0 | 20001 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU079_IU_Exist | 246 | IU079_IU_Exist | 3 | 20224 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU079_OnOff_status | 246 | IU079_OnOff_status | 3 | 20225 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU079_OnOff_command | 246 | IU079_OnOff_command | 4 | 20226 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU079_Mode_status | 246 | IU079_Mode_status | 13 | 20227 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU079_Mode_command | 246 | IU079_Mode_command | 14 | 20228 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU079_SetPoint_status | 246 | IU079_SetPoint_status | 0 | 20229 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU079_SetPoint_command | 246 | IU079_SetPoint_command | 1 | 20230 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU079_Room_Temperature | 246 | IU079_Room_Temperature | 0 | 20231 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU079_FanSpeed_status | 246 | IU079_FanSpeed_status | 13 | 20232 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU079_FanSpeed_command | 246 | IU079_FanSpeed_command | 14 | 20233 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU079_AirDirection_status | 246 | IU079_AirDirection_status | 13 | 20234 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU079_AirDirection_command | 246 | IU079_AirDirection_command | 14 | 20235 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU079_FilterSign_status | 246 | IU079_FilterSign_status | 3 | 20236 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU079_FilterSign_Reset_command | 246 | IU079_FilterSign_Reset_command | 4 | 20237 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU079_ErrorCode | 246 | IU079_ErrorCode | 13/0** | 20238 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU079_RemoteControl_Lock | 246 | IU079_RemoteControl_Lock | 19 | 20239 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU079_Occupancy | 246 | IU079_Occupancy | 19 | 20254 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU079_Consumption_Yesterday | 246 | IU079_Consumption_Yesterday | 0 | 20255 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU079_Consumption_Today | 246 | IU079_Consumption_Today | 0 | 20256 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU079_Consumption_Total | 246 | IU079_Consumption_Total | 0 | 20257 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU080_IU_Exist | 246 | IU080_IU_Exist | 3 | 20480 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU080_OnOff_status | 246 | IU080_OnOff_status | 3 | 20481 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU080_OnOff_command | 246 | IU080_OnOff_command | 4 | 20482 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU080_Mode_status | 246 | IU080_Mode_status | 13 | 20483 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU080_Mode_command | 246 | IU080_Mode_command | 14 | 20484 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU080_SetPoint_status | 246 | IU080_SetPoint_status | 0 | 20485 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU080_SetPoint_command | 246 | IU080_SetPoint_command | 1 | 20486 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU080_Room_Temperature | 246 | IU080_Room_Temperature | 0 | 20487 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU080_FanSpeed_status | 246 | IU080_FanSpeed_status | 13 | 20488 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU080_FanSpeed_command | 246 | IU080_FanSpeed_command | 14 | 20489 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU080_AirDirection_status | 246 | IU080_AirDirection_status | 13 | 20490 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU080_AirDirection_command | 246 | IU080_AirDirection_command | 14 | 20491 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU080_FilterSign_status | 246 | IU080_FilterSign_status | 3 | 20492 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU080_FilterSign_Reset_command | 246 | IU080_FilterSign_Reset_command | 4 | 20493 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU080_ErrorCode | 246 | IU080_ErrorCode | 13/0** | 20494 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU080_RemoteControl_Lock | 246 | IU080_RemoteControl_Lock | 19 | 20495 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU080_Occupancy | 246 | IU080_Occupancy | 19 | 20510 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU080_Consumption_Yesterday | 246 | IU080_Consumption_Yesterday | 0 | 20511 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU080_Consumption_Today | 246 | IU080_Consumption_Today | 0 | 20512 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU080_Consumption_Total | 246 | IU080_Consumption_Total | 0 | 20513 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU081_IU_Exist | 246 | IU081_IU_Exist | 3 | 20736 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU081_OnOff_status | 246 | IU081_OnOff_status | 3 | 20737 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU081_OnOff_command | 246 | IU081_OnOff_command | 4 | 20738 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU081_Mode_status | 246 | IU081_Mode_status | 13 | 20739 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU081_Mode_command | 246 | IU081_Mode_command | 14 | 20740 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU081_SetPoint_status | 246 | IU081_SetPoint_status | 0 | 20741 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU081_SetPoint_command | 246 | IU081_SetPoint_command | 1 | 20742 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU081_Room_Temperature | 246 | IU081_Room_Temperature | 0 | 20743 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU081_FanSpeed_status | 246 | IU081_FanSpeed_status | 13 | 20744 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU081_FanSpeed_command | 246 | IU081_FanSpeed_command | 14 | 20745 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU081_AirDirection_status | 246 | IU081_AirDirection_status | 13 | 20746 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU081_AirDirection_command | 246 | IU081_AirDirection_command | 14 | 20747 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU081_FilterSign_status | 246 | IU081_FilterSign_status | 3 | 20748 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU081_FilterSign_Reset_command | 246 | IU081_FilterSign_Reset_command | 4 | 20749 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU081_ErrorCode | 246 | IU081_ErrorCode | 13/0** | 20750 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU081_RemoteControl_Lock | 246 | IU081_RemoteControl_Lock | 19 | 20751 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU081_Occupancy | 246 | IU081_Occupancy | 19 | 20766 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU081_Consumption_Yesterday | 246 | IU081_Consumption_Yesterday | 0 | 20767 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU081_Consumption_Today | 246 | IU081_Consumption_Today | 0 | 20768 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU081_Consumption_Total | 246 | IU081_Consumption_Total | 0 | 20769 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU082_IU_Exist | 246 | IU082_IU_Exist | 3 | 20992 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU082_OnOff_status | 246 | IU082_OnOff_status | 3 | 20993 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU082_OnOff_command | 246 | IU082_OnOff_command | 4 | 20994 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU082_Mode_status | 246 | IU082_Mode_status | 13 | 20995 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU082_Mode_command | 246 | IU082_Mode_command | 14 | 20996 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU082_SetPoint_status | 246 | IU082_SetPoint_status | 0 | 20997 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU082_SetPoint_command | 246 | IU082_SetPoint_command | 1 | 20998 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU082_Room_Temperature | 246 | IU082_Room_Temperature | 0 | 20999 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU082_FanSpeed_status | 246 | IU082_FanSpeed_status | 13 | 21000 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU082_FanSpeed_command | 246 | IU082_FanSpeed_command | 14 | 21001 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU082_AirDirection_status | 246 | IU082_AirDirection_status | 13 | 21002 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU082_AirDirection_command | 246 | IU082_AirDirection_command | 14 | 21003 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU082_FilterSign_status | 246 | IU082_FilterSign_status | 3 | 21004 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU082_FilterSign_Reset_command | 246 | IU082_FilterSign_Reset_command | 4 | 21005 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU082_ErrorCode | 246 | IU082_ErrorCode | 13/0** | 21006 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU082_RemoteControl_Lock | 246 | IU082_RemoteControl_Lock | 19 | 21007 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU082_Occupancy | 246 | IU082_Occupancy | 19 | 21022 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU082_Consumption_Yesterday | 246 | IU082_Consumption_Yesterday | 0 | 21023 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU082_Consumption_Today | 246 | IU082_Consumption_Today | 0 | 21024 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU082_Consumption_Total | 246 | IU082_Consumption_Total | 0 | 21025 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU083_IU_Exist | 246 | IU083_IU_Exist | 3 | 21248 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU083_OnOff_status | 246 | IU083_OnOff_status | 3 | 21249 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU083_OnOff_command | 246 | IU083_OnOff_command | 4 | 21250 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU083_Mode_status | 246 | IU083_Mode_status | 13 | 21251 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU083_Mode_command | 246 | IU083_Mode_command | 14 | 21252 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU083_SetPoint_status | 246 | IU083_SetPoint_status | 0 | 21253 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU083_SetPoint_command | 246 | IU083_SetPoint_command | 1 | 21254 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU083_Room_Temperature | 246 | IU083_Room_Temperature | 0 | 21255 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU083_FanSpeed_status | 246 | IU083_FanSpeed_status | 13 | 21256 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU083_FanSpeed_command | 246 | IU083_FanSpeed_command | 14 | 21257 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU083_AirDirection_status | 246 | IU083_AirDirection_status | 13 | 21258 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU083_AirDirection_command | 246 | IU083_AirDirection_command | 14 | 21259 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU083_FilterSign_status | 246 | IU083_FilterSign_status | 3 | 21260 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU083_FilterSign_Reset_command | 246 | IU083_FilterSign_Reset_command | 4 | 21261 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU083_ErrorCode | 246 | IU083_ErrorCode | 13/0** | 21262 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU083_RemoteControl_Lock | 246 | IU083_RemoteControl_Lock | 19 | 21263 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU083_Occupancy | 246 | IU083_Occupancy | 19 | 21278 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU083_Consumption_Yesterday | 246 | IU083_Consumption_Yesterday | 0 | 21279 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU083_Consumption_Today | 246 | IU083_Consumption_Today | 0 | 21280 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU083_Consumption_Total | 246 | IU083_Consumption_Total | 0 | 21281 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU084_IU_Exist | 246 | IU084_IU_Exist | 3 | 21504 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU084_OnOff_status | 246 | IU084_OnOff_status | 3 | 21505 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU084_OnOff_command | 246 | IU084_OnOff_command | 4 | 21506 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU084_Mode_status | 246 | IU084_Mode_status | 13 | 21507 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU084_Mode_command | 246 | IU084_Mode_command | 14 | 21508 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU084_SetPoint_status | 246 | IU084_SetPoint_status | 0 | 21509 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU084_SetPoint_command | 246 | IU084_SetPoint_command | 1 | 21510 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU084_Room_Temperature | 246 | IU084_Room_Temperature | 0 | 21511 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU084_FanSpeed_status | 246 | IU084_FanSpeed_status | 13 | 21512 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU084_FanSpeed_command | 246 | IU084_FanSpeed_command | 14 | 21513 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU084_AirDirection_status | 246 | IU084_AirDirection_status | 13 | 21514 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU084_AirDirection_command | 246 | IU084_AirDirection_command | 14 | 21515 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU084_FilterSign_status | 246 | IU084_FilterSign_status | 3 | 21516 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU084_FilterSign_Reset_command | 246 | IU084_FilterSign_Reset_command | 4 | 21517 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU084_ErrorCode | 246 | IU084_ErrorCode | 13/0** | 21518 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU084_RemoteControl_Lock | 246 | IU084_RemoteControl_Lock | 19 | 21519 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU084_Occupancy | 246 | IU084_Occupancy | 19 | 21534 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU084_Consumption_Yesterday | 246 | IU084_Consumption_Yesterday | 0 | 21535 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU084_Consumption_Today | 246 | IU084_Consumption_Today | 0 | 21536 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU084_Consumption_Total | 246 | IU084_Consumption_Total | 0 | 21537 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU085_IU_Exist | 246 | IU085_IU_Exist | 3 | 21760 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU085_OnOff_status | 246 | IU085_OnOff_status | 3 | 21761 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU085_OnOff_command | 246 | IU085_OnOff_command | 4 | 21762 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU085_Mode_status | 246 | IU085_Mode_status | 13 | 21763 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU085_Mode_command | 246 | IU085_Mode_command | 14 | 21764 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU085_SetPoint_status | 246 | IU085_SetPoint_status | 0 | 21765 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU085_SetPoint_command | 246 | IU085_SetPoint_command | 1 | 21766 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU085_Room_Temperature | 246 | IU085_Room_Temperature | 0 | 21767 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU085_FanSpeed_status | 246 | IU085_FanSpeed_status | 13 | 21768 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU085_FanSpeed_command | 246 | IU085_FanSpeed_command | 14 | 21769 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU085_AirDirection_status | 246 | IU085_AirDirection_status | 13 | 21770 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU085_AirDirection_command | 246 | IU085_AirDirection_command | 14 | 21771 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU085_FilterSign_status | 246 | IU085_FilterSign_status | 3 | 21772 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU085_FilterSign_Reset_command | 246 | IU085_FilterSign_Reset_command | 4 | 21773 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU085_ErrorCode | 246 | IU085_ErrorCode | 13/0** | 21774 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU085_RemoteControl_Lock | 246 | IU085_RemoteControl_Lock | 19 | 21775 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU085_Occupancy | 246 | IU085_Occupancy | 19 | 21790 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU085_Consumption_Yesterday | 246 | IU085_Consumption_Yesterday | 0 | 21791 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU085_Consumption_Today | 246 | IU085_Consumption_Today | 0 | 21792 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU085_Consumption_Total | 246 | IU085_Consumption_Total | 0 | 21793 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU086_IU_Exist | 246 | IU086_IU_Exist | 3 | 22016 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU086_OnOff_status | 246 | IU086_OnOff_status | 3 | 22017 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU086_OnOff_command | 246 | IU086_OnOff_command | 4 | 22018 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU086_Mode_status | 246 | IU086_Mode_status | 13 | 22019 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU086_Mode_command | 246 | IU086_Mode_command | 14 | 22020 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU086_SetPoint_status | 246 | IU086_SetPoint_status | 0 | 22021 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU086_SetPoint_command | 246 | IU086_SetPoint_command | 1 | 22022 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU086_Room_Temperature | 246 | IU086_Room_Temperature | 0 | 22023 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU086_FanSpeed_status | 246 | IU086_FanSpeed_status | 13 | 22024 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU086_FanSpeed_command | 246 | IU086_FanSpeed_command | 14 | 22025 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU086_AirDirection_status | 246 | IU086_AirDirection_status | 13 | 22026 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU086_AirDirection_command | 246 | IU086_AirDirection_command | 14 | 22027 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU086_FilterSign_status | 246 | IU086_FilterSign_status | 3 | 22028 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU086_FilterSign_Reset_command | 246 | IU086_FilterSign_Reset_command | 4 | 22029 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU086_ErrorCode | 246 | IU086_ErrorCode | 13/0** | 22030 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU086_RemoteControl_Lock | 246 | IU086_RemoteControl_Lock | 19 | 22031 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU086_Occupancy | 246 | IU086_Occupancy | 19 | 22046 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU086_Consumption_Yesterday | 246 | IU086_Consumption_Yesterday | 0 | 22047 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU086_Consumption_Today | 246 | IU086_Consumption_Today | 0 | 22048 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU086_Consumption_Total | 246 | IU086_Consumption_Total | 0 | 22049 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU087_IU_Exist | 246 | IU087_IU_Exist | 3 | 22272 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU087_OnOff_status | 246 | IU087_OnOff_status | 3 | 22273 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU087_OnOff_command | 246 | IU087_OnOff_command | 4 | 22274 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU087_Mode_status | 246 | IU087_Mode_status | 13 | 22275 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU087_Mode_command | 246 | IU087_Mode_command | 14 | 22276 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU087_SetPoint_status | 246 | IU087_SetPoint_status | 0 | 22277 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU087_SetPoint_command | 246 | IU087_SetPoint_command | 1 | 22278 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU087_Room_Temperature | 246 | IU087_Room_Temperature | 0 | 22279 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU087_FanSpeed_status | 246 | IU087_FanSpeed_status | 13 | 22280 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU087_FanSpeed_command | 246 | IU087_FanSpeed_command | 14 | 22281 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU087_AirDirection_status | 246 | IU087_AirDirection_status | 13 | 22282 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU087_AirDirection_command | 246 | IU087_AirDirection_command | 14 | 22283 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU087_FilterSign_status | 246 | IU087_FilterSign_status | 3 | 22284 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU087_FilterSign_Reset_command | 246 | IU087_FilterSign_Reset_command | 4 | 22285 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU087_ErrorCode | 246 | IU087_ErrorCode | 13/0** | 22286 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU087_RemoteControl_Lock | 246 | IU087_RemoteControl_Lock | 19 | 22287 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU087_Occupancy | 246 | IU087_Occupancy | 19 | 22302 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU087_Consumption_Yesterday | 246 | IU087_Consumption_Yesterday | 0 | 22303 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU087_Consumption_Today | 246 | IU087_Consumption_Today | 0 | 22304 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU087_Consumption_Total | 246 | IU087_Consumption_Total | 0 | 22305 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU088_IU_Exist | 246 | IU088_IU_Exist | 3 | 22528 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU088_OnOff_status | 246 | IU088_OnOff_status | 3 | 22529 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU088_OnOff_command | 246 | IU088_OnOff_command | 4 | 22530 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU088_Mode_status | 246 | IU088_Mode_status | 13 | 22531 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU088_Mode_command | 246 | IU088_Mode_command | 14 | 22532 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU088_SetPoint_status | 246 | IU088_SetPoint_status | 0 | 22533 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU088_SetPoint_command | 246 | IU088_SetPoint_command | 1 | 22534 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU088_Room_Temperature | 246 | IU088_Room_Temperature | 0 | 22535 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU088_FanSpeed_status | 246 | IU088_FanSpeed_status | 13 | 22536 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU088_FanSpeed_command | 246 | IU088_FanSpeed_command | 14 | 22537 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU088_AirDirection_status | 246 | IU088_AirDirection_status | 13 | 22538 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU088_AirDirection_command | 246 | IU088_AirDirection_command | 14 | 22539 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU088_FilterSign_status | 246 | IU088_FilterSign_status | 3 | 22540 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU088_FilterSign_Reset_command | 246 | IU088_FilterSign_Reset_command | 4 | 22541 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU088_ErrorCode | 246 | IU088_ErrorCode | 13/0** | 22542 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU088_RemoteControl_Lock | 246 | IU088_RemoteControl_Lock | 19 | 22543 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU088_Occupancy | 246 | IU088_Occupancy | 19 | 22558 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU088_Consumption_Yesterday | 246 | IU088_Consumption_Yesterday | 0 | 22559 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU088_Consumption_Today | 246 | IU088_Consumption_Today | 0 | 22560 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU088_Consumption_Total | 246 | IU088_Consumption_Total | 0 | 22561 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU089_IU_Exist | 246 | IU089_IU_Exist | 3 | 22784 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU089_OnOff_status | 246 | IU089_OnOff_status | 3 | 22785 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU089_OnOff_command | 246 | IU089_OnOff_command | 4 | 22786 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU089_Mode_status | 246 | IU089_Mode_status | 13 | 22787 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU089_Mode_command | 246 | IU089_Mode_command | 14 | 22788 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU089_SetPoint_status | 246 | IU089_SetPoint_status | 0 | 22789 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU089_SetPoint_command | 246 | IU089_SetPoint_command | 1 | 22790 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU089_Room_Temperature | 246 | IU089_Room_Temperature | 0 | 22791 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU089_FanSpeed_status | 246 | IU089_FanSpeed_status | 13 | 22792 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU089_FanSpeed_command | 246 | IU089_FanSpeed_command | 14 | 22793 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU089_AirDirection_status | 246 | IU089_AirDirection_status | 13 | 22794 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU089_AirDirection_command | 246 | IU089_AirDirection_command | 14 | 22795 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU089_FilterSign_status | 246 | IU089_FilterSign_status | 3 | 22796 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU089_FilterSign_Reset_command | 246 | IU089_FilterSign_Reset_command | 4 | 22797 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU089_ErrorCode | 246 | IU089_ErrorCode | 13/0** | 22798 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU089_RemoteControl_Lock | 246 | IU089_RemoteControl_Lock | 19 | 22799 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU089_Occupancy | 246 | IU089_Occupancy | 19 | 22814 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU089_Consumption_Yesterday | 246 | IU089_Consumption_Yesterday | 0 | 22815 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU089_Consumption_Today | 246 | IU089_Consumption_Today | 0 | 22816 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU089_Consumption_Total | 246 | IU089_Consumption_Total | 0 | 22817 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU090_IU_Exist | 246 | IU090_IU_Exist | 3 | 23040 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU090_OnOff_status | 246 | IU090_OnOff_status | 3 | 23041 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU090_OnOff_command | 246 | IU090_OnOff_command | 4 | 23042 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU090_Mode_status | 246 | IU090_Mode_status | 13 | 23043 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU090_Mode_command | 246 | IU090_Mode_command | 14 | 23044 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU090_SetPoint_status | 246 | IU090_SetPoint_status | 0 | 23045 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU090_SetPoint_command | 246 | IU090_SetPoint_command | 1 | 23046 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU090_Room_Temperature | 246 | IU090_Room_Temperature | 0 | 23047 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU090_FanSpeed_status | 246 | IU090_FanSpeed_status | 13 | 23048 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU090_FanSpeed_command | 246 | IU090_FanSpeed_command | 14 | 23049 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU090_AirDirection_status | 246 | IU090_AirDirection_status | 13 | 23050 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU090_AirDirection_command | 246 | IU090_AirDirection_command | 14 | 23051 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU090_FilterSign_status | 246 | IU090_FilterSign_status | 3 | 23052 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU090_FilterSign_Reset_command | 246 | IU090_FilterSign_Reset_command | 4 | 23053 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU090_ErrorCode | 246 | IU090_ErrorCode | 13/0** | 23054 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU090_RemoteControl_Lock | 246 | IU090_RemoteControl_Lock | 19 | 23055 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU090_Occupancy | 246 | IU090_Occupancy | 19 | 23070 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU090_Consumption_Yesterday | 246 | IU090_Consumption_Yesterday | 0 | 23071 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU090_Consumption_Today | 246 | IU090_Consumption_Today | 0 | 23072 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU090_Consumption_Total | 246 | IU090_Consumption_Total | 0 | 23073 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU091_IU_Exist | 246 | IU091_IU_Exist | 3 | 23296 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU091_OnOff_status | 246 | IU091_OnOff_status | 3 | 23297 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU091_OnOff_command | 246 | IU091_OnOff_command | 4 | 23298 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU091_Mode_status | 246 | IU091_Mode_status | 13 | 23299 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU091_Mode_command | 246 | IU091_Mode_command | 14 | 23300 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU091_SetPoint_status | 246 | IU091_SetPoint_status | 0 | 23301 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU091_SetPoint_command | 246 | IU091_SetPoint_command | 1 | 23302 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU091_Room_Temperature | 246 | IU091_Room_Temperature | 0 | 23303 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU091_FanSpeed_status | 246 | IU091_FanSpeed_status | 13 | 23304 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU091_FanSpeed_command | 246 | IU091_FanSpeed_command | 14 | 23305 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU091_AirDirection_status | 246 | IU091_AirDirection_status | 13 | 23306 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU091_AirDirection_command | 246 | IU091_AirDirection_command | 14 | 23307 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU091_FilterSign_status | 246 | IU091_FilterSign_status | 3 | 23308 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU091_FilterSign_Reset_command | 246 | IU091_FilterSign_Reset_command | 4 | 23309 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU091_ErrorCode | 246 | IU091_ErrorCode | 13/0** | 23310 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU091_RemoteControl_Lock | 246 | IU091_RemoteControl_Lock | 19 | 23311 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU091_Occupancy | 246 | IU091_Occupancy | 19 | 23326 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU091_Consumption_Yesterday | 246 | IU091_Consumption_Yesterday | 0 | 23327 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU091_Consumption_Today | 246 | IU091_Consumption_Today | 0 | 23328 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU091_Consumption_Total | 246 | IU091_Consumption_Total | 0 | 23329 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU092_IU_Exist | 246 | IU092_IU_Exist | 3 | 23552 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU092_OnOff_status | 246 | IU092_OnOff_status | 3 | 23553 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU092_OnOff_command | 246 | IU092_OnOff_command | 4 | 23554 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU092_Mode_status | 246 | IU092_Mode_status | 13 | 23555 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU092_Mode_command | 246 | IU092_Mode_command | 14 | 23556 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU092_SetPoint_status | 246 | IU092_SetPoint_status | 0 | 23557 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU092_SetPoint_command | 246 | IU092_SetPoint_command | 1 | 23558 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU092_Room_Temperature | 246 | IU092_Room_Temperature | 0 | 23559 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU092_FanSpeed_status | 246 | IU092_FanSpeed_status | 13 | 23560 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU092_FanSpeed_command | 246 | IU092_FanSpeed_command | 14 | 23561 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU092_AirDirection_status | 246 | IU092_AirDirection_status | 13 | 23562 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU092_AirDirection_command | 246 | IU092_AirDirection_command | 14 | 23563 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU092_FilterSign_status | 246 | IU092_FilterSign_status | 3 | 23564 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU092_FilterSign_Reset_command | 246 | IU092_FilterSign_Reset_command | 4 | 23565 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU092_ErrorCode | 246 | IU092_ErrorCode | 13/0** | 23566 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU092_RemoteControl_Lock | 246 | IU092_RemoteControl_Lock | 19 | 23567 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU092_Occupancy | 246 | IU092_Occupancy | 19 | 23582 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU092_Consumption_Yesterday | 246 | IU092_Consumption_Yesterday | 0 | 23583 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU092_Consumption_Today | 246 | IU092_Consumption_Today | 0 | 23584 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU092_Consumption_Total | 246 | IU092_Consumption_Total | 0 | 23585 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU093_IU_Exist | 246 | IU093_IU_Exist | 3 | 23808 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU093_OnOff_status | 246 | IU093_OnOff_status | 3 | 23809 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU093_OnOff_command | 246 | IU093_OnOff_command | 4 | 23810 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU093_Mode_status | 246 | IU093_Mode_status | 13 | 23811 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU093_Mode_command | 246 | IU093_Mode_command | 14 | 23812 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU093_SetPoint_status | 246 | IU093_SetPoint_status | 0 | 23813 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU093_SetPoint_command | 246 | IU093_SetPoint_command | 1 | 23814 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU093_Room_Temperature | 246 | IU093_Room_Temperature | 0 | 23815 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU093_FanSpeed_status | 246 | IU093_FanSpeed_status | 13 | 23816 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU093_FanSpeed_command | 246 | IU093_FanSpeed_command | 14 | 23817 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU093_AirDirection_status | 246 | IU093_AirDirection_status | 13 | 23818 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU093_AirDirection_command | 246 | IU093_AirDirection_command | 14 | 23819 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU093_FilterSign_status | 246 | IU093_FilterSign_status | 3 | 23820 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU093_FilterSign_Reset_command | 246 | IU093_FilterSign_Reset_command | 4 | 23821 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU093_ErrorCode | 246 | IU093_ErrorCode | 13/0** | 23822 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU093_RemoteControl_Lock | 246 | IU093_RemoteControl_Lock | 19 | 23823 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU093_Occupancy | 246 | IU093_Occupancy | 19 | 23838 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU093_Consumption_Yesterday | 246 | IU093_Consumption_Yesterday | 0 | 23839 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU093_Consumption_Today | 246 | IU093_Consumption_Today | 0 | 23840 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU093_Consumption_Total | 246 | IU093_Consumption_Total | 0 | 23841 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU094_IU_Exist | 246 | IU094_IU_Exist | 3 | 24064 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU094_OnOff_status | 246 | IU094_OnOff_status | 3 | 24065 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU094_OnOff_command | 246 | IU094_OnOff_command | 4 | 24066 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU094_Mode_status | 246 | IU094_Mode_status | 13 | 24067 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU094_Mode_command | 246 | IU094_Mode_command | 14 | 24068 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU094_SetPoint_status | 246 | IU094_SetPoint_status | 0 | 24069 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU094_SetPoint_command | 246 | IU094_SetPoint_command | 1 | 24070 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU094_Room_Temperature | 246 | IU094_Room_Temperature | 0 | 24071 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU094_FanSpeed_status | 246 | IU094_FanSpeed_status | 13 | 24072 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU094_FanSpeed_command | 246 | IU094_FanSpeed_command | 14 | 24073 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU094_AirDirection_status | 246 | IU094_AirDirection_status | 13 | 24074 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU094_AirDirection_command | 246 | IU094_AirDirection_command | 14 | 24075 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU094_FilterSign_status | 246 | IU094_FilterSign_status | 3 | 24076 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU094_FilterSign_Reset_command | 246 | IU094_FilterSign_Reset_command | 4 | 24077 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU094_ErrorCode | 246 | IU094_ErrorCode | 13/0** | 24078 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU094_RemoteControl_Lock | 246 | IU094_RemoteControl_Lock | 19 | 24079 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU094_Occupancy | 246 | IU094_Occupancy | 19 | 24094 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU094_Consumption_Yesterday | 246 | IU094_Consumption_Yesterday | 0 | 24095 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU094_Consumption_Today | 246 | IU094_Consumption_Today | 0 | 24096 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU094_Consumption_Total | 246 | IU094_Consumption_Total | 0 | 24097 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU095_IU_Exist | 246 | IU095_IU_Exist | 3 | 24320 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU095_OnOff_status | 246 | IU095_OnOff_status | 3 | 24321 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU095_OnOff_command | 246 | IU095_OnOff_command | 4 | 24322 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU095_Mode_status | 246 | IU095_Mode_status | 13 | 24323 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU095_Mode_command | 246 | IU095_Mode_command | 14 | 24324 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU095_SetPoint_status | 246 | IU095_SetPoint_status | 0 | 24325 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU095_SetPoint_command | 246 | IU095_SetPoint_command | 1 | 24326 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU095_Room_Temperature | 246 | IU095_Room_Temperature | 0 | 24327 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU095_FanSpeed_status | 246 | IU095_FanSpeed_status | 13 | 24328 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU095_FanSpeed_command | 246 | IU095_FanSpeed_command | 14 | 24329 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU095_AirDirection_status | 246 | IU095_AirDirection_status | 13 | 24330 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU095_AirDirection_command | 246 | IU095_AirDirection_command | 14 | 24331 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU095_FilterSign_status | 246 | IU095_FilterSign_status | 3 | 24332 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU095_FilterSign_Reset_command | 246 | IU095_FilterSign_Reset_command | 4 | 24333 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU095_ErrorCode | 246 | IU095_ErrorCode | 13/0** | 24334 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU095_RemoteControl_Lock | 246 | IU095_RemoteControl_Lock | 19 | 24335 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU095_Occupancy | 246 | IU095_Occupancy | 19 | 24350 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU095_Consumption_Yesterday | 246 | IU095_Consumption_Yesterday | 0 | 24351 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU095_Consumption_Today | 246 | IU095_Consumption_Today | 0 | 24352 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU095_Consumption_Total | 246 | IU095_Consumption_Total | 0 | 24353 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU096_IU_Exist | 246 | IU096_IU_Exist | 3 | 24576 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU096_OnOff_status | 246 | IU096_OnOff_status | 3 | 24577 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU096_OnOff_command | 246 | IU096_OnOff_command | 4 | 24578 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU096_Mode_status | 246 | IU096_Mode_status | 13 | 24579 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU096_Mode_command | 246 | IU096_Mode_command | 14 | 24580 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU096_SetPoint_status | 246 | IU096_SetPoint_status | 0 | 24581 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU096_SetPoint_command | 246 | IU096_SetPoint_command | 1 | 24582 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU096_Room_Temperature | 246 | IU096_Room_Temperature | 0 | 24583 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU096_FanSpeed_status | 246 | IU096_FanSpeed_status | 13 | 24584 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU096_FanSpeed_command | 246 | IU096_FanSpeed_command | 14 | 24585 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU096_AirDirection_status | 246 | IU096_AirDirection_status | 13 | 24586 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU096_AirDirection_command | 246 | IU096_AirDirection_command | 14 | 24587 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU096_FilterSign_status | 246 | IU096_FilterSign_status | 3 | 24588 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU096_FilterSign_Reset_command | 246 | IU096_FilterSign_Reset_command | 4 | 24589 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU096_ErrorCode | 246 | IU096_ErrorCode | 13/0** | 24590 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU096_RemoteControl_Lock | 246 | IU096_RemoteControl_Lock | 19 | 24591 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU096_Occupancy | 246 | IU096_Occupancy | 19 | 24606 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU096_Consumption_Yesterday | 246 | IU096_Consumption_Yesterday | 0 | 24607 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU096_Consumption_Today | 246 | IU096_Consumption_Today | 0 | 24608 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU096_Consumption_Total | 246 | IU096_Consumption_Total | 0 | 24609 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU097_IU_Exist | 246 | IU097_IU_Exist | 3 | 24832 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU097_OnOff_status | 246 | IU097_OnOff_status | 3 | 24833 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU097_OnOff_command | 246 | IU097_OnOff_command | 4 | 24834 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU097_Mode_status | 246 | IU097_Mode_status | 13 | 24835 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU097_Mode_command | 246 | IU097_Mode_command | 14 | 24836 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU097_SetPoint_status | 246 | IU097_SetPoint_status | 0 | 24837 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU097_SetPoint_command | 246 | IU097_SetPoint_command | 1 | 24838 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU097_Room_Temperature | 246 | IU097_Room_Temperature | 0 | 24839 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU097_FanSpeed_status | 246 | IU097_FanSpeed_status | 13 | 24840 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU097_FanSpeed_command | 246 | IU097_FanSpeed_command | 14 | 24841 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU097_AirDirection_status | 246 | IU097_AirDirection_status | 13 | 24842 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU097_AirDirection_command | 246 | IU097_AirDirection_command | 14 | 24843 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU097_FilterSign_status | 246 | IU097_FilterSign_status | 3 | 24844 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU097_FilterSign_Reset_command | 246 | IU097_FilterSign_Reset_command | 4 | 24845 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU097_ErrorCode | 246 | IU097_ErrorCode | 13/0** | 24846 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU097_RemoteControl_Lock | 246 | IU097_RemoteControl_Lock | 19 | 24847 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU097_Occupancy | 246 | IU097_Occupancy | 19 | 24862 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU097_Consumption_Yesterday | 246 | IU097_Consumption_Yesterday | 0 | 24863 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU097_Consumption_Today | 246 | IU097_Consumption_Today | 0 | 24864 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU097_Consumption_Total | 246 | IU097_Consumption_Total | 0 | 24865 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU098_IU_Exist | 246 | IU098_IU_Exist | 3 | 25088 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU098_OnOff_status | 246 | IU098_OnOff_status | 3 | 25089 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU098_OnOff_command | 246 | IU098_OnOff_command | 4 | 25090 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU098_Mode_status | 246 | IU098_Mode_status | 13 | 25091 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU098_Mode_command | 246 | IU098_Mode_command | 14 | 25092 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU098_SetPoint_status | 246 | IU098_SetPoint_status | 0 | 25093 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU098_SetPoint_command | 246 | IU098_SetPoint_command | 1 | 25094 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU098_Room_Temperature | 246 | IU098_Room_Temperature | 0 | 25095 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU098_FanSpeed_status | 246 | IU098_FanSpeed_status | 13 | 25096 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU098_FanSpeed_command | 246 | IU098_FanSpeed_command | 14 | 25097 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU098_AirDirection_status | 246 | IU098_AirDirection_status | 13 | 25098 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU098_AirDirection_command | 246 | IU098_AirDirection_command | 14 | 25099 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU098_FilterSign_status | 246 | IU098_FilterSign_status | 3 | 25100 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU098_FilterSign_Reset_command | 246 | IU098_FilterSign_Reset_command | 4 | 25101 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU098_ErrorCode | 246 | IU098_ErrorCode | 13/0** | 25102 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU098_RemoteControl_Lock | 246 | IU098_RemoteControl_Lock | 19 | 25103 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU098_Occupancy | 246 | IU098_Occupancy | 19 | 25118 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU098_Consumption_Yesterday | 246 | IU098_Consumption_Yesterday | 0 | 25119 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU098_Consumption_Today | 246 | IU098_Consumption_Today | 0 | 25120 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU098_Consumption_Total | 246 | IU098_Consumption_Total | 0 | 25121 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU099_IU_Exist | 246 | IU099_IU_Exist | 3 | 25344 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU099_OnOff_status | 246 | IU099_OnOff_status | 3 | 25345 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU099_OnOff_command | 246 | IU099_OnOff_command | 4 | 25346 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU099_Mode_status | 246 | IU099_Mode_status | 13 | 25347 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU099_Mode_command | 246 | IU099_Mode_command | 14 | 25348 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU099_SetPoint_status | 246 | IU099_SetPoint_status | 0 | 25349 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU099_SetPoint_command | 246 | IU099_SetPoint_command | 1 | 25350 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU099_Room_Temperature | 246 | IU099_Room_Temperature | 0 | 25351 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU099_FanSpeed_status | 246 | IU099_FanSpeed_status | 13 | 25352 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU099_FanSpeed_command | 246 | IU099_FanSpeed_command | 14 | 25353 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU099_AirDirection_status | 246 | IU099_AirDirection_status | 13 | 25354 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU099_AirDirection_command | 246 | IU099_AirDirection_command | 14 | 25355 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU099_FilterSign_status | 246 | IU099_FilterSign_status | 3 | 25356 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU099_FilterSign_Reset_command | 246 | IU099_FilterSign_Reset_command | 4 | 25357 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU099_ErrorCode | 246 | IU099_ErrorCode | 13/0** | 25358 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU099_RemoteControl_Lock | 246 | IU099_RemoteControl_Lock | 19 | 25359 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU099_Occupancy | 246 | IU099_Occupancy | 19 | 25374 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU099_Consumption_Yesterday | 246 | IU099_Consumption_Yesterday | 0 | 25375 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU099_Consumption_Today | 246 | IU099_Consumption_Today | 0 | 25376 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU099_Consumption_Total | 246 | IU099_Consumption_Total | 0 | 25377 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU100_IU_Exist | 246 | IU100_IU_Exist | 3 | 25600 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU100_OnOff_status | 246 | IU100_OnOff_status | 3 | 25601 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU100_OnOff_command | 246 | IU100_OnOff_command | 4 | 25602 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU100_Mode_status | 246 | IU100_Mode_status | 13 | 25603 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU100_Mode_command | 246 | IU100_Mode_command | 14 | 25604 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU100_SetPoint_status | 246 | IU100_SetPoint_status | 0 | 25605 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU100_SetPoint_command | 246 | IU100_SetPoint_command | 1 | 25606 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU100_Room_Temperature | 246 | IU100_Room_Temperature | 0 | 25607 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU100_FanSpeed_status | 246 | IU100_FanSpeed_status | 13 | 25608 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU100_FanSpeed_command | 246 | IU100_FanSpeed_command | 14 | 25609 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU100_AirDirection_status | 246 | IU100_AirDirection_status | 13 | 25610 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU100_AirDirection_command | 246 | IU100_AirDirection_command | 14 | 25611 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU100_FilterSign_status | 246 | IU100_FilterSign_status | 3 | 25612 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU100_FilterSign_Reset_command | 246 | IU100_FilterSign_Reset_command | 4 | 25613 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU100_ErrorCode | 246 | IU100_ErrorCode | 13/0** | 25614 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU100_RemoteControl_Lock | 246 | IU100_RemoteControl_Lock | 19 | 25615 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU100_Occupancy | 246 | IU100_Occupancy | 19 | 25630 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU100_Consumption_Yesterday | 246 | IU100_Consumption_Yesterday | 0 | 25631 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU100_Consumption_Today | 246 | IU100_Consumption_Today | 0 | 25632 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU100_Consumption_Total | 246 | IU100_Consumption_Total | 0 | 25633 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU101_IU_Exist | 246 | IU101_IU_Exist | 3 | 25856 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU101_OnOff_status | 246 | IU101_OnOff_status | 3 | 25857 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU101_OnOff_command | 246 | IU101_OnOff_command | 4 | 25858 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU101_Mode_status | 246 | IU101_Mode_status | 13 | 25859 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU101_Mode_command | 246 | IU101_Mode_command | 14 | 25860 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU101_SetPoint_status | 246 | IU101_SetPoint_status | 0 | 25861 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU101_SetPoint_command | 246 | IU101_SetPoint_command | 1 | 25862 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU101_Room_Temperature | 246 | IU101_Room_Temperature | 0 | 25863 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU101_FanSpeed_status | 246 | IU101_FanSpeed_status | 13 | 25864 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU101_FanSpeed_command | 246 | IU101_FanSpeed_command | 14 | 25865 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU101_AirDirection_status | 246 | IU101_AirDirection_status | 13 | 25866 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU101_AirDirection_command | 246 | IU101_AirDirection_command | 14 | 25867 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU101_FilterSign_status | 246 | IU101_FilterSign_status | 3 | 25868 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU101_FilterSign_Reset_command | 246 | IU101_FilterSign_Reset_command | 4 | 25869 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU101_ErrorCode | 246 | IU101_ErrorCode | 13/0** | 25870 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU101_RemoteControl_Lock | 246 | IU101_RemoteControl_Lock | 19 | 25871 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU101_Occupancy | 246 | IU101_Occupancy | 19 | 25886 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU101_Consumption_Yesterday | 246 | IU101_Consumption_Yesterday | 0 | 25887 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU101_Consumption_Today | 246 | IU101_Consumption_Today | 0 | 25888 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU101_Consumption_Total | 246 | IU101_Consumption_Total | 0 | 25889 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU102_IU_Exist | 246 | IU102_IU_Exist | 3 | 26112 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU102_OnOff_status | 246 | IU102_OnOff_status | 3 | 26113 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU102_OnOff_command | 246 | IU102_OnOff_command | 4 | 26114 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU102_Mode_status | 246 | IU102_Mode_status | 13 | 26115 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU102_Mode_command | 246 | IU102_Mode_command | 14 | 26116 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU102_SetPoint_status | 246 | IU102_SetPoint_status | 0 | 26117 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU102_SetPoint_command | 246 | IU102_SetPoint_command | 1 | 26118 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU102_Room_Temperature | 246 | IU102_Room_Temperature | 0 | 26119 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU102_FanSpeed_status | 246 | IU102_FanSpeed_status | 13 | 26120 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU102_FanSpeed_command | 246 | IU102_FanSpeed_command | 14 | 26121 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU102_AirDirection_status | 246 | IU102_AirDirection_status | 13 | 26122 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU102_AirDirection_command | 246 | IU102_AirDirection_command | 14 | 26123 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU102_FilterSign_status | 246 | IU102_FilterSign_status | 3 | 26124 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU102_FilterSign_Reset_command | 246 | IU102_FilterSign_Reset_command | 4 | 26125 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU102_ErrorCode | 246 | IU102_ErrorCode | 13/0** | 26126 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU102_RemoteControl_Lock | 246 | IU102_RemoteControl_Lock | 19 | 26127 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU102_Occupancy | 246 | IU102_Occupancy | 19 | 26142 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU102_Consumption_Yesterday | 246 | IU102_Consumption_Yesterday | 0 | 26143 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU102_Consumption_Today | 246 | IU102_Consumption_Today | 0 | 26144 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU102_Consumption_Total | 246 | IU102_Consumption_Total | 0 | 26145 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU103_IU_Exist | 246 | IU103_IU_Exist | 3 | 26368 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU103_OnOff_status | 246 | IU103_OnOff_status | 3 | 26369 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU103_OnOff_command | 246 | IU103_OnOff_command | 4 | 26370 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU103_Mode_status | 246 | IU103_Mode_status | 13 | 26371 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU103_Mode_command | 246 | IU103_Mode_command | 14 | 26372 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU103_SetPoint_status | 246 | IU103_SetPoint_status | 0 | 26373 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU103_SetPoint_command | 246 | IU103_SetPoint_command | 1 | 26374 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU103_Room_Temperature | 246 | IU103_Room_Temperature | 0 | 26375 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU103_FanSpeed_status | 246 | IU103_FanSpeed_status | 13 | 26376 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU103_FanSpeed_command | 246 | IU103_FanSpeed_command | 14 | 26377 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU103_AirDirection_status | 246 | IU103_AirDirection_status | 13 | 26378 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU103_AirDirection_command | 246 | IU103_AirDirection_command | 14 | 26379 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU103_FilterSign_status | 246 | IU103_FilterSign_status | 3 | 26380 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU103_FilterSign_Reset_command | 246 | IU103_FilterSign_Reset_command | 4 | 26381 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU103_ErrorCode | 246 | IU103_ErrorCode | 13/0** | 26382 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU103_RemoteControl_Lock | 246 | IU103_RemoteControl_Lock | 19 | 26383 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU103_Occupancy | 246 | IU103_Occupancy | 19 | 26398 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU103_Consumption_Yesterday | 246 | IU103_Consumption_Yesterday | 0 | 26399 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU103_Consumption_Today | 246 | IU103_Consumption_Today | 0 | 26400 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU103_Consumption_Total | 246 | IU103_Consumption_Total | 0 | 26401 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU104_IU_Exist | 246 | IU104_IU_Exist | 3 | 26624 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU104_OnOff_status | 246 | IU104_OnOff_status | 3 | 26625 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU104_OnOff_command | 246 | IU104_OnOff_command | 4 | 26626 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU104_Mode_status | 246 | IU104_Mode_status | 13 | 26627 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU104_Mode_command | 246 | IU104_Mode_command | 14 | 26628 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU104_SetPoint_status | 246 | IU104_SetPoint_status | 0 | 26629 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU104_SetPoint_command | 246 | IU104_SetPoint_command | 1 | 26630 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU104_Room_Temperature | 246 | IU104_Room_Temperature | 0 | 26631 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU104_FanSpeed_status | 246 | IU104_FanSpeed_status | 13 | 26632 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU104_FanSpeed_command | 246 | IU104_FanSpeed_command | 14 | 26633 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU104_AirDirection_status | 246 | IU104_AirDirection_status | 13 | 26634 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU104_AirDirection_command | 246 | IU104_AirDirection_command | 14 | 26635 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU104_FilterSign_status | 246 | IU104_FilterSign_status | 3 | 26636 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU104_FilterSign_Reset_command | 246 | IU104_FilterSign_Reset_command | 4 | 26637 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU104_ErrorCode | 246 | IU104_ErrorCode | 13/0** | 26638 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU104_RemoteControl_Lock | 246 | IU104_RemoteControl_Lock | 19 | 26639 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU104_Occupancy | 246 | IU104_Occupancy | 19 | 26654 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU104_Consumption_Yesterday | 246 | IU104_Consumption_Yesterday | 0 | 26655 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU104_Consumption_Today | 246 | IU104_Consumption_Today | 0 | 26656 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU104_Consumption_Total | 246 | IU104_Consumption_Total | 0 | 26657 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU105_IU_Exist | 246 | IU105_IU_Exist | 3 | 26880 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU105_OnOff_status | 246 | IU105_OnOff_status | 3 | 26881 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU105_OnOff_command | 246 | IU105_OnOff_command | 4 | 26882 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU105_Mode_status | 246 | IU105_Mode_status | 13 | 26883 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU105_Mode_command | 246 | IU105_Mode_command | 14 | 26884 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU105_SetPoint_status | 246 | IU105_SetPoint_status | 0 | 26885 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU105_SetPoint_command | 246 | IU105_SetPoint_command | 1 | 26886 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU105_Room_Temperature | 246 | IU105_Room_Temperature | 0 | 26887 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU105_FanSpeed_status | 246 | IU105_FanSpeed_status | 13 | 26888 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU105_FanSpeed_command | 246 | IU105_FanSpeed_command | 14 | 26889 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU105_AirDirection_status | 246 | IU105_AirDirection_status | 13 | 26890 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU105_AirDirection_command | 246 | IU105_AirDirection_command | 14 | 26891 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU105_FilterSign_status | 246 | IU105_FilterSign_status | 3 | 26892 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU105_FilterSign_Reset_command | 246 | IU105_FilterSign_Reset_command | 4 | 26893 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU105_ErrorCode | 246 | IU105_ErrorCode | 13/0** | 26894 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU105_RemoteControl_Lock | 246 | IU105_RemoteControl_Lock | 19 | 26895 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU105_Occupancy | 246 | IU105_Occupancy | 19 | 26910 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU105_Consumption_Yesterday | 246 | IU105_Consumption_Yesterday | 0 | 26911 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU105_Consumption_Today | 246 | IU105_Consumption_Today | 0 | 26912 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU105_Consumption_Total | 246 | IU105_Consumption_Total | 0 | 26913 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU106_IU_Exist | 246 | IU106_IU_Exist | 3 | 27136 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU106_OnOff_status | 246 | IU106_OnOff_status | 3 | 27137 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU106_OnOff_command | 246 | IU106_OnOff_command | 4 | 27138 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU106_Mode_status | 246 | IU106_Mode_status | 13 | 27139 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU106_Mode_command | 246 | IU106_Mode_command | 14 | 27140 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU106_SetPoint_status | 246 | IU106_SetPoint_status | 0 | 27141 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU106_SetPoint_command | 246 | IU106_SetPoint_command | 1 | 27142 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU106_Room_Temperature | 246 | IU106_Room_Temperature | 0 | 27143 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU106_FanSpeed_status | 246 | IU106_FanSpeed_status | 13 | 27144 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU106_FanSpeed_command | 246 | IU106_FanSpeed_command | 14 | 27145 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU106_AirDirection_status | 246 | IU106_AirDirection_status | 13 | 27146 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU106_AirDirection_command | 246 | IU106_AirDirection_command | 14 | 27147 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU106_FilterSign_status | 246 | IU106_FilterSign_status | 3 | 27148 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU106_FilterSign_Reset_command | 246 | IU106_FilterSign_Reset_command | 4 | 27149 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU106_ErrorCode | 246 | IU106_ErrorCode | 13/0** | 27150 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU106_RemoteControl_Lock | 246 | IU106_RemoteControl_Lock | 19 | 27151 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU106_Occupancy | 246 | IU106_Occupancy | 19 | 27166 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU106_Consumption_Yesterday | 246 | IU106_Consumption_Yesterday | 0 | 27167 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU106_Consumption_Today | 246 | IU106_Consumption_Today | 0 | 27168 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU106_Consumption_Total | 246 | IU106_Consumption_Total | 0 | 27169 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU107_IU_Exist | 246 | IU107_IU_Exist | 3 | 27392 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU107_OnOff_status | 246 | IU107_OnOff_status | 3 | 27393 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU107_OnOff_command | 246 | IU107_OnOff_command | 4 | 27394 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU107_Mode_status | 246 | IU107_Mode_status | 13 | 27395 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU107_Mode_command | 246 | IU107_Mode_command | 14 | 27396 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU107_SetPoint_status | 246 | IU107_SetPoint_status | 0 | 27397 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU107_SetPoint_command | 246 | IU107_SetPoint_command | 1 | 27398 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU107_Room_Temperature | 246 | IU107_Room_Temperature | 0 | 27399 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU107_FanSpeed_status | 246 | IU107_FanSpeed_status | 13 | 27400 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU107_FanSpeed_command | 246 | IU107_FanSpeed_command | 14 | 27401 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU107_AirDirection_status | 246 | IU107_AirDirection_status | 13 | 27402 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU107_AirDirection_command | 246 | IU107_AirDirection_command | 14 | 27403 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU107_FilterSign_status | 246 | IU107_FilterSign_status | 3 | 27404 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU107_FilterSign_Reset_command | 246 | IU107_FilterSign_Reset_command | 4 | 27405 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU107_ErrorCode | 246 | IU107_ErrorCode | 13/0** | 27406 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU107_RemoteControl_Lock | 246 | IU107_RemoteControl_Lock | 19 | 27407 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU107_Occupancy | 246 | IU107_Occupancy | 19 | 27422 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU107_Consumption_Yesterday | 246 | IU107_Consumption_Yesterday | 0 | 27423 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU107_Consumption_Today | 246 | IU107_Consumption_Today | 0 | 27424 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU107_Consumption_Total | 246 | IU107_Consumption_Total | 0 | 27425 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU108_IU_Exist | 246 | IU108_IU_Exist | 3 | 27648 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU108_OnOff_status | 246 | IU108_OnOff_status | 3 | 27649 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU108_OnOff_command | 246 | IU108_OnOff_command | 4 | 27650 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU108_Mode_status | 246 | IU108_Mode_status | 13 | 27651 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU108_Mode_command | 246 | IU108_Mode_command | 14 | 27652 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU108_SetPoint_status | 246 | IU108_SetPoint_status | 0 | 27653 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU108_SetPoint_command | 246 | IU108_SetPoint_command | 1 | 27654 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU108_Room_Temperature | 246 | IU108_Room_Temperature | 0 | 27655 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU108_FanSpeed_status | 246 | IU108_FanSpeed_status | 13 | 27656 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU108_FanSpeed_command | 246 | IU108_FanSpeed_command | 14 | 27657 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU108_AirDirection_status | 246 | IU108_AirDirection_status | 13 | 27658 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU108_AirDirection_command | 246 | IU108_AirDirection_command | 14 | 27659 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU108_FilterSign_status | 246 | IU108_FilterSign_status | 3 | 27660 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU108_FilterSign_Reset_command | 246 | IU108_FilterSign_Reset_command | 4 | 27661 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU108_ErrorCode | 246 | IU108_ErrorCode | 13/0** | 27662 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU108_RemoteControl_Lock | 246 | IU108_RemoteControl_Lock | 19 | 27663 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU108_Occupancy | 246 | IU108_Occupancy | 19 | 27678 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU108_Consumption_Yesterday | 246 | IU108_Consumption_Yesterday | 0 | 27679 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU108_Consumption_Today | 246 | IU108_Consumption_Today | 0 | 27680 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU108_Consumption_Total | 246 | IU108_Consumption_Total | 0 | 27681 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU109_IU_Exist | 246 | IU109_IU_Exist | 3 | 27904 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU109_OnOff_status | 246 | IU109_OnOff_status | 3 | 27905 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU109_OnOff_command | 246 | IU109_OnOff_command | 4 | 27906 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU109_Mode_status | 246 | IU109_Mode_status | 13 | 27907 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU109_Mode_command | 246 | IU109_Mode_command | 14 | 27908 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU109_SetPoint_status | 246 | IU109_SetPoint_status | 0 | 27909 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU109_SetPoint_command | 246 | IU109_SetPoint_command | 1 | 27910 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU109_Room_Temperature | 246 | IU109_Room_Temperature | 0 | 27911 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU109_FanSpeed_status | 246 | IU109_FanSpeed_status | 13 | 27912 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU109_FanSpeed_command | 246 | IU109_FanSpeed_command | 14 | 27913 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU109_AirDirection_status | 246 | IU109_AirDirection_status | 13 | 27914 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU109_AirDirection_command | 246 | IU109_AirDirection_command | 14 | 27915 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU109_FilterSign_status | 246 | IU109_FilterSign_status | 3 | 27916 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU109_FilterSign_Reset_command | 246 | IU109_FilterSign_Reset_command | 4 | 27917 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU109_ErrorCode | 246 | IU109_ErrorCode | 13/0** | 27918 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU109_RemoteControl_Lock | 246 | IU109_RemoteControl_Lock | 19 | 27919 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU109_Occupancy | 246 | IU109_Occupancy | 19 | 27934 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU109_Consumption_Yesterday | 246 | IU109_Consumption_Yesterday | 0 | 27935 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU109_Consumption_Today | 246 | IU109_Consumption_Today | 0 | 27936 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU109_Consumption_Total | 246 | IU109_Consumption_Total | 0 | 27937 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU110_IU_Exist | 246 | IU110_IU_Exist | 3 | 28160 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU110_OnOff_status | 246 | IU110_OnOff_status | 3 | 28161 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU110_OnOff_command | 246 | IU110_OnOff_command | 4 | 28162 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU110_Mode_status | 246 | IU110_Mode_status | 13 | 28163 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU110_Mode_command | 246 | IU110_Mode_command | 14 | 28164 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU110_SetPoint_status | 246 | IU110_SetPoint_status | 0 | 28165 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU110_SetPoint_command | 246 | IU110_SetPoint_command | 1 | 28166 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU110_Room_Temperature | 246 | IU110_Room_Temperature | 0 | 28167 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU110_FanSpeed_status | 246 | IU110_FanSpeed_status | 13 | 28168 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU110_FanSpeed_command | 246 | IU110_FanSpeed_command | 14 | 28169 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU110_AirDirection_status | 246 | IU110_AirDirection_status | 13 | 28170 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU110_AirDirection_command | 246 | IU110_AirDirection_command | 14 | 28171 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU110_FilterSign_status | 246 | IU110_FilterSign_status | 3 | 28172 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU110_FilterSign_Reset_command | 246 | IU110_FilterSign_Reset_command | 4 | 28173 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU110_ErrorCode | 246 | IU110_ErrorCode | 13/0** | 28174 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU110_RemoteControl_Lock | 246 | IU110_RemoteControl_Lock | 19 | 28175 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU110_Occupancy | 246 | IU110_Occupancy | 19 | 28190 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU110_Consumption_Yesterday | 246 | IU110_Consumption_Yesterday | 0 | 28191 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU110_Consumption_Today | 246 | IU110_Consumption_Today | 0 | 28192 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU110_Consumption_Total | 246 | IU110_Consumption_Total | 0 | 28193 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU111_IU_Exist | 246 | IU111_IU_Exist | 3 | 28416 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU111_OnOff_status | 246 | IU111_OnOff_status | 3 | 28417 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU111_OnOff_command | 246 | IU111_OnOff_command | 4 | 28418 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU111_Mode_status | 246 | IU111_Mode_status | 13 | 28419 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU111_Mode_command | 246 | IU111_Mode_command | 14 | 28420 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU111_SetPoint_status | 246 | IU111_SetPoint_status | 0 | 28421 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU111_SetPoint_command | 246 | IU111_SetPoint_command | 1 | 28422 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU111_Room_Temperature | 246 | IU111_Room_Temperature | 0 | 28423 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU111_FanSpeed_status | 246 | IU111_FanSpeed_status | 13 | 28424 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU111_FanSpeed_command | 246 | IU111_FanSpeed_command | 14 | 28425 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU111_AirDirection_status | 246 | IU111_AirDirection_status | 13 | 28426 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU111_AirDirection_command | 246 | IU111_AirDirection_command | 14 | 28427 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU111_FilterSign_status | 246 | IU111_FilterSign_status | 3 | 28428 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU111_FilterSign_Reset_command | 246 | IU111_FilterSign_Reset_command | 4 | 28429 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU111_ErrorCode | 246 | IU111_ErrorCode | 13/0** | 28430 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU111_RemoteControl_Lock | 246 | IU111_RemoteControl_Lock | 19 | 28431 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU111_Occupancy | 246 | IU111_Occupancy | 19 | 28446 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU111_Consumption_Yesterday | 246 | IU111_Consumption_Yesterday | 0 | 28447 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU111_Consumption_Today | 246 | IU111_Consumption_Today | 0 | 28448 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU111_Consumption_Total | 246 | IU111_Consumption_Total | 0 | 28449 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU112_IU_Exist | 246 | IU112_IU_Exist | 3 | 28672 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU112_OnOff_status | 246 | IU112_OnOff_status | 3 | 28673 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU112_OnOff_command | 246 | IU112_OnOff_command | 4 | 28674 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU112_Mode_status | 246 | IU112_Mode_status | 13 | 28675 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU112_Mode_command | 246 | IU112_Mode_command | 14 | 28676 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU112_SetPoint_status | 246 | IU112_SetPoint_status | 0 | 28677 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU112_SetPoint_command | 246 | IU112_SetPoint_command | 1 | 28678 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU112_Room_Temperature | 246 | IU112_Room_Temperature | 0 | 28679 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU112_FanSpeed_status | 246 | IU112_FanSpeed_status | 13 | 28680 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU112_FanSpeed_command | 246 | IU112_FanSpeed_command | 14 | 28681 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU112_AirDirection_status | 246 | IU112_AirDirection_status | 13 | 28682 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU112_AirDirection_command | 246 | IU112_AirDirection_command | 14 | 28683 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU112_FilterSign_status | 246 | IU112_FilterSign_status | 3 | 28684 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU112_FilterSign_Reset_command | 246 | IU112_FilterSign_Reset_command | 4 | 28685 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU112_ErrorCode | 246 | IU112_ErrorCode | 13/0** | 28686 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU112_RemoteControl_Lock | 246 | IU112_RemoteControl_Lock | 19 | 28687 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU112_Occupancy | 246 | IU112_Occupancy | 19 | 28702 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU112_Consumption_Yesterday | 246 | IU112_Consumption_Yesterday | 0 | 28703 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU112_Consumption_Today | 246 | IU112_Consumption_Today | 0 | 28704 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU112_Consumption_Total | 246 | IU112_Consumption_Total | 0 | 28705 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU113_IU_Exist | 246 | IU113_IU_Exist | 3 | 28928 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU113_OnOff_status | 246 | IU113_OnOff_status | 3 | 28929 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU113_OnOff_command | 246 | IU113_OnOff_command | 4 | 28930 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU113_Mode_status | 246 | IU113_Mode_status | 13 | 28931 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU113_Mode_command | 246 | IU113_Mode_command | 14 | 28932 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU113_SetPoint_status | 246 | IU113_SetPoint_status | 0 | 28933 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU113_SetPoint_command | 246 | IU113_SetPoint_command | 1 | 28934 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU113_Room_Temperature | 246 | IU113_Room_Temperature | 0 | 28935 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU113_FanSpeed_status | 246 | IU113_FanSpeed_status | 13 | 28936 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU113_FanSpeed_command | 246 | IU113_FanSpeed_command | 14 | 28937 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU113_AirDirection_status | 246 | IU113_AirDirection_status | 13 | 28938 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU113_AirDirection_command | 246 | IU113_AirDirection_command | 14 | 28939 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU113_FilterSign_status | 246 | IU113_FilterSign_status | 3 | 28940 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU113_FilterSign_Reset_command | 246 | IU113_FilterSign_Reset_command | 4 | 28941 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU113_ErrorCode | 246 | IU113_ErrorCode | 13/0** | 28942 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU113_RemoteControl_Lock | 246 | IU113_RemoteControl_Lock | 19 | 28943 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU113_Occupancy | 246 | IU113_Occupancy | 19 | 28958 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU113_Consumption_Yesterday | 246 | IU113_Consumption_Yesterday | 0 | 28959 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU113_Consumption_Today | 246 | IU113_Consumption_Today | 0 | 28960 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU113_Consumption_Total | 246 | IU113_Consumption_Total | 0 | 28961 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU114_IU_Exist | 246 | IU114_IU_Exist | 3 | 29184 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU114_OnOff_status | 246 | IU114_OnOff_status | 3 | 29185 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU114_OnOff_command | 246 | IU114_OnOff_command | 4 | 29186 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU114_Mode_status | 246 | IU114_Mode_status | 13 | 29187 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU114_Mode_command | 246 | IU114_Mode_command | 14 | 29188 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU114_SetPoint_status | 246 | IU114_SetPoint_status | 0 | 29189 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU114_SetPoint_command | 246 | IU114_SetPoint_command | 1 | 29190 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU114_Room_Temperature | 246 | IU114_Room_Temperature | 0 | 29191 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU114_FanSpeed_status | 246 | IU114_FanSpeed_status | 13 | 29192 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU114_FanSpeed_command | 246 | IU114_FanSpeed_command | 14 | 29193 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU114_AirDirection_status | 246 | IU114_AirDirection_status | 13 | 29194 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU114_AirDirection_command | 246 | IU114_AirDirection_command | 14 | 29195 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU114_FilterSign_status | 246 | IU114_FilterSign_status | 3 | 29196 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU114_FilterSign_Reset_command | 246 | IU114_FilterSign_Reset_command | 4 | 29197 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU114_ErrorCode | 246 | IU114_ErrorCode | 13/0** | 29198 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU114_RemoteControl_Lock | 246 | IU114_RemoteControl_Lock | 19 | 29199 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU114_Occupancy | 246 | IU114_Occupancy | 19 | 29214 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU114_Consumption_Yesterday | 246 | IU114_Consumption_Yesterday | 0 | 29215 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU114_Consumption_Today | 246 | IU114_Consumption_Today | 0 | 29216 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU114_Consumption_Total | 246 | IU114_Consumption_Total | 0 | 29217 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU115_IU_Exist | 246 | IU115_IU_Exist | 3 | 29440 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU115_OnOff_status | 246 | IU115_OnOff_status | 3 | 29441 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU115_OnOff_command | 246 | IU115_OnOff_command | 4 | 29442 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU115_Mode_status | 246 | IU115_Mode_status | 13 | 29443 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU115_Mode_command | 246 | IU115_Mode_command | 14 | 29444 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU115_SetPoint_status | 246 | IU115_SetPoint_status | 0 | 29445 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU115_SetPoint_command | 246 | IU115_SetPoint_command | 1 | 29446 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU115_Room_Temperature | 246 | IU115_Room_Temperature | 0 | 29447 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU115_FanSpeed_status | 246 | IU115_FanSpeed_status | 13 | 29448 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU115_FanSpeed_command | 246 | IU115_FanSpeed_command | 14 | 29449 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU115_AirDirection_status | 246 | IU115_AirDirection_status | 13 | 29450 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU115_AirDirection_command | 246 | IU115_AirDirection_command | 14 | 29451 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU115_FilterSign_status | 246 | IU115_FilterSign_status | 3 | 29452 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU115_FilterSign_Reset_command | 246 | IU115_FilterSign_Reset_command | 4 | 29453 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU115_ErrorCode | 246 | IU115_ErrorCode | 13/0** | 29454 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU115_RemoteControl_Lock | 246 | IU115_RemoteControl_Lock | 19 | 29455 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU115_Occupancy | 246 | IU115_Occupancy | 19 | 29470 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU115_Consumption_Yesterday | 246 | IU115_Consumption_Yesterday | 0 | 29471 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU115_Consumption_Today | 246 | IU115_Consumption_Today | 0 | 29472 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU115_Consumption_Total | 246 | IU115_Consumption_Total | 0 | 29473 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU116_IU_Exist | 246 | IU116_IU_Exist | 3 | 29696 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU116_OnOff_status | 246 | IU116_OnOff_status | 3 | 29697 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU116_OnOff_command | 246 | IU116_OnOff_command | 4 | 29698 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU116_Mode_status | 246 | IU116_Mode_status | 13 | 29699 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU116_Mode_command | 246 | IU116_Mode_command | 14 | 29700 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU116_SetPoint_status | 246 | IU116_SetPoint_status | 0 | 29701 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU116_SetPoint_command | 246 | IU116_SetPoint_command | 1 | 29702 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU116_Room_Temperature | 246 | IU116_Room_Temperature | 0 | 29703 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU116_FanSpeed_status | 246 | IU116_FanSpeed_status | 13 | 29704 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU116_FanSpeed_command | 246 | IU116_FanSpeed_command | 14 | 29705 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU116_AirDirection_status | 246 | IU116_AirDirection_status | 13 | 29706 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU116_AirDirection_command | 246 | IU116_AirDirection_command | 14 | 29707 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU116_FilterSign_status | 246 | IU116_FilterSign_status | 3 | 29708 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU116_FilterSign_Reset_command | 246 | IU116_FilterSign_Reset_command | 4 | 29709 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU116_ErrorCode | 246 | IU116_ErrorCode | 13/0** | 29710 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU116_RemoteControl_Lock | 246 | IU116_RemoteControl_Lock | 19 | 29711 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU116_Occupancy | 246 | IU116_Occupancy | 19 | 29726 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU116_Consumption_Yesterday | 246 | IU116_Consumption_Yesterday | 0 | 29727 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU116_Consumption_Today | 246 | IU116_Consumption_Today | 0 | 29728 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU116_Consumption_Total | 246 | IU116_Consumption_Total | 0 | 29729 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU117_IU_Exist | 246 | IU117_IU_Exist | 3 | 29952 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU117_OnOff_status | 246 | IU117_OnOff_status | 3 | 29953 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU117_OnOff_command | 246 | IU117_OnOff_command | 4 | 29954 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU117_Mode_status | 246 | IU117_Mode_status | 13 | 29955 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU117_Mode_command | 246 | IU117_Mode_command | 14 | 29956 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU117_SetPoint_status | 246 | IU117_SetPoint_status | 0 | 29957 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU117_SetPoint_command | 246 | IU117_SetPoint_command | 1 | 29958 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU117_Room_Temperature | 246 | IU117_Room_Temperature | 0 | 29959 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU117_FanSpeed_status | 246 | IU117_FanSpeed_status | 13 | 29960 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU117_FanSpeed_command | 246 | IU117_FanSpeed_command | 14 | 29961 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU117_AirDirection_status | 246 | IU117_AirDirection_status | 13 | 29962 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU117_AirDirection_command | 246 | IU117_AirDirection_command | 14 | 29963 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU117_FilterSign_status | 246 | IU117_FilterSign_status | 3 | 29964 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU117_FilterSign_Reset_command | 246 | IU117_FilterSign_Reset_command | 4 | 29965 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU117_ErrorCode | 246 | IU117_ErrorCode | 13/0** | 29966 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU117_RemoteControl_Lock | 246 | IU117_RemoteControl_Lock | 19 | 29967 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU117_Occupancy | 246 | IU117_Occupancy | 19 | 29982 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU117_Consumption_Yesterday | 246 | IU117_Consumption_Yesterday | 0 | 29983 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU117_Consumption_Today | 246 | IU117_Consumption_Today | 0 | 29984 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU117_Consumption_Total | 246 | IU117_Consumption_Total | 0 | 29985 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU118_IU_Exist | 246 | IU118_IU_Exist | 3 | 30208 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU118_OnOff_status | 246 | IU118_OnOff_status | 3 | 30209 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU118_OnOff_command | 246 | IU118_OnOff_command | 4 | 30210 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU118_Mode_status | 246 | IU118_Mode_status | 13 | 30211 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU118_Mode_command | 246 | IU118_Mode_command | 14 | 30212 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU118_SetPoint_status | 246 | IU118_SetPoint_status | 0 | 30213 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU118_SetPoint_command | 246 | IU118_SetPoint_command | 1 | 30214 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU118_Room_Temperature | 246 | IU118_Room_Temperature | 0 | 30215 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU118_FanSpeed_status | 246 | IU118_FanSpeed_status | 13 | 30216 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU118_FanSpeed_command | 246 | IU118_FanSpeed_command | 14 | 30217 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU118_AirDirection_status | 246 | IU118_AirDirection_status | 13 | 30218 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU118_AirDirection_command | 246 | IU118_AirDirection_command | 14 | 30219 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU118_FilterSign_status | 246 | IU118_FilterSign_status | 3 | 30220 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU118_FilterSign_Reset_command | 246 | IU118_FilterSign_Reset_command | 4 | 30221 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU118_ErrorCode | 246 | IU118_ErrorCode | 13/0** | 30222 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU118_RemoteControl_Lock | 246 | IU118_RemoteControl_Lock | 19 | 30223 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU118_Occupancy | 246 | IU118_Occupancy | 19 | 30238 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU118_Consumption_Yesterday | 246 | IU118_Consumption_Yesterday | 0 | 30239 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU118_Consumption_Today | 246 | IU118_Consumption_Today | 0 | 30240 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU118_Consumption_Total | 246 | IU118_Consumption_Total | 0 | 30241 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU119_IU_Exist | 246 | IU119_IU_Exist | 3 | 30464 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU119_OnOff_status | 246 | IU119_OnOff_status | 3 | 30465 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU119_OnOff_command | 246 | IU119_OnOff_command | 4 | 30466 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU119_Mode_status | 246 | IU119_Mode_status | 13 | 30467 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU119_Mode_command | 246 | IU119_Mode_command | 14 | 30468 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU119_SetPoint_status | 246 | IU119_SetPoint_status | 0 | 30469 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU119_SetPoint_command | 246 | IU119_SetPoint_command | 1 | 30470 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU119_Room_Temperature | 246 | IU119_Room_Temperature | 0 | 30471 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU119_FanSpeed_status | 246 | IU119_FanSpeed_status | 13 | 30472 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU119_FanSpeed_command | 246 | IU119_FanSpeed_command | 14 | 30473 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU119_AirDirection_status | 246 | IU119_AirDirection_status | 13 | 30474 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU119_AirDirection_command | 246 | IU119_AirDirection_command | 14 | 30475 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU119_FilterSign_status | 246 | IU119_FilterSign_status | 3 | 30476 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU119_FilterSign_Reset_command | 246 | IU119_FilterSign_Reset_command | 4 | 30477 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU119_ErrorCode | 246 | IU119_ErrorCode | 13/0** | 30478 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU119_RemoteControl_Lock | 246 | IU119_RemoteControl_Lock | 19 | 30479 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU119_Occupancy | 246 | IU119_Occupancy | 19 | 30494 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU119_Consumption_Yesterday | 246 | IU119_Consumption_Yesterday | 0 | 30495 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU119_Consumption_Today | 246 | IU119_Consumption_Today | 0 | 30496 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU119_Consumption_Total | 246 | IU119_Consumption_Total | 0 | 30497 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU120_IU_Exist | 246 | IU120_IU_Exist | 3 | 30720 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU120_OnOff_status | 246 | IU120_OnOff_status | 3 | 30721 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU120_OnOff_command | 246 | IU120_OnOff_command | 4 | 30722 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU120_Mode_status | 246 | IU120_Mode_status | 13 | 30723 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU120_Mode_command | 246 | IU120_Mode_command | 14 | 30724 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU120_SetPoint_status | 246 | IU120_SetPoint_status | 0 | 30725 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU120_SetPoint_command | 246 | IU120_SetPoint_command | 1 | 30726 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU120_Room_Temperature | 246 | IU120_Room_Temperature | 0 | 30727 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU120_FanSpeed_status | 246 | IU120_FanSpeed_status | 13 | 30728 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU120_FanSpeed_command | 246 | IU120_FanSpeed_command | 14 | 30729 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU120_AirDirection_status | 246 | IU120_AirDirection_status | 13 | 30730 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU120_AirDirection_command | 246 | IU120_AirDirection_command | 14 | 30731 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU120_FilterSign_status | 246 | IU120_FilterSign_status | 3 | 30732 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU120_FilterSign_Reset_command | 246 | IU120_FilterSign_Reset_command | 4 | 30733 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU120_ErrorCode | 246 | IU120_ErrorCode | 13/0** | 30734 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU120_RemoteControl_Lock | 246 | IU120_RemoteControl_Lock | 19 | 30735 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU120_Occupancy | 246 | IU120_Occupancy | 19 | 30750 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU120_Consumption_Yesterday | 246 | IU120_Consumption_Yesterday | 0 | 30751 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU120_Consumption_Today | 246 | IU120_Consumption_Today | 0 | 30752 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU120_Consumption_Total | 246 | IU120_Consumption_Total | 0 | 30753 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU121_IU_Exist | 246 | IU121_IU_Exist | 3 | 30976 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU121_OnOff_status | 246 | IU121_OnOff_status | 3 | 30977 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU121_OnOff_command | 246 | IU121_OnOff_command | 4 | 30978 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU121_Mode_status | 246 | IU121_Mode_status | 13 | 30979 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU121_Mode_command | 246 | IU121_Mode_command | 14 | 30980 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU121_SetPoint_status | 246 | IU121_SetPoint_status | 0 | 30981 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU121_SetPoint_command | 246 | IU121_SetPoint_command | 1 | 30982 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU121_Room_Temperature | 246 | IU121_Room_Temperature | 0 | 30983 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU121_FanSpeed_status | 246 | IU121_FanSpeed_status | 13 | 30984 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU121_FanSpeed_command | 246 | IU121_FanSpeed_command | 14 | 30985 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU121_AirDirection_status | 246 | IU121_AirDirection_status | 13 | 30986 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU121_AirDirection_command | 246 | IU121_AirDirection_command | 14 | 30987 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU121_FilterSign_status | 246 | IU121_FilterSign_status | 3 | 30988 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU121_FilterSign_Reset_command | 246 | IU121_FilterSign_Reset_command | 4 | 30989 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU121_ErrorCode | 246 | IU121_ErrorCode | 13/0** | 30990 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU121_RemoteControl_Lock | 246 | IU121_RemoteControl_Lock | 19 | 30991 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU121_Occupancy | 246 | IU121_Occupancy | 19 | 31006 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU121_Consumption_Yesterday | 246 | IU121_Consumption_Yesterday | 0 | 31007 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU121_Consumption_Today | 246 | IU121_Consumption_Today | 0 | 31008 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU121_Consumption_Total | 246 | IU121_Consumption_Total | 0 | 31009 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU122_IU_Exist | 246 | IU122_IU_Exist | 3 | 31232 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU122_OnOff_status | 246 | IU122_OnOff_status | 3 | 31233 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU122_OnOff_command | 246 | IU122_OnOff_command | 4 | 31234 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU122_Mode_status | 246 | IU122_Mode_status | 13 | 31235 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU122_Mode_command | 246 | IU122_Mode_command | 14 | 31236 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU122_SetPoint_status | 246 | IU122_SetPoint_status | 0 | 31237 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU122_SetPoint_command | 246 | IU122_SetPoint_command | 1 | 31238 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU122_Room_Temperature | 246 | IU122_Room_Temperature | 0 | 31239 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU122_FanSpeed_status | 246 | IU122_FanSpeed_status | 13 | 31240 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU122_FanSpeed_command | 246 | IU122_FanSpeed_command | 14 | 31241 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU122_AirDirection_status | 246 | IU122_AirDirection_status | 13 | 31242 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU122_AirDirection_command | 246 | IU122_AirDirection_command | 14 | 31243 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU122_FilterSign_status | 246 | IU122_FilterSign_status | 3 | 31244 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU122_FilterSign_Reset_command | 246 | IU122_FilterSign_Reset_command | 4 | 31245 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU122_ErrorCode | 246 | IU122_ErrorCode | 13/0** | 31246 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU122_RemoteControl_Lock | 246 | IU122_RemoteControl_Lock | 19 | 31247 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU122_Occupancy | 246 | IU122_Occupancy | 19 | 31262 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU122_Consumption_Yesterday | 246 | IU122_Consumption_Yesterday | 0 | 31263 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU122_Consumption_Today | 246 | IU122_Consumption_Today | 0 | 31264 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU122_Consumption_Total | 246 | IU122_Consumption_Total | 0 | 31265 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU123_IU_Exist | 246 | IU123_IU_Exist | 3 | 31488 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU123_OnOff_status | 246 | IU123_OnOff_status | 3 | 31489 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU123_OnOff_command | 246 | IU123_OnOff_command | 4 | 31490 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU123_Mode_status | 246 | IU123_Mode_status | 13 | 31491 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU123_Mode_command | 246 | IU123_Mode_command | 14 | 31492 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU123_SetPoint_status | 246 | IU123_SetPoint_status | 0 | 31493 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU123_SetPoint_command | 246 | IU123_SetPoint_command | 1 | 31494 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU123_Room_Temperature | 246 | IU123_Room_Temperature | 0 | 31495 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU123_FanSpeed_status | 246 | IU123_FanSpeed_status | 13 | 31496 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU123_FanSpeed_command | 246 | IU123_FanSpeed_command | 14 | 31497 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU123_AirDirection_status | 246 | IU123_AirDirection_status | 13 | 31498 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU123_AirDirection_command | 246 | IU123_AirDirection_command | 14 | 31499 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU123_FilterSign_status | 246 | IU123_FilterSign_status | 3 | 31500 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU123_FilterSign_Reset_command | 246 | IU123_FilterSign_Reset_command | 4 | 31501 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU123_ErrorCode | 246 | IU123_ErrorCode | 13/0** | 31502 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU123_RemoteControl_Lock | 246 | IU123_RemoteControl_Lock | 19 | 31503 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU123_Occupancy | 246 | IU123_Occupancy | 19 | 31518 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU123_Consumption_Yesterday | 246 | IU123_Consumption_Yesterday | 0 | 31519 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU123_Consumption_Today | 246 | IU123_Consumption_Today | 0 | 31520 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU123_Consumption_Total | 246 | IU123_Consumption_Total | 0 | 31521 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU124_IU_Exist | 246 | IU124_IU_Exist | 3 | 31744 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU124_OnOff_status | 246 | IU124_OnOff_status | 3 | 31745 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU124_OnOff_command | 246 | IU124_OnOff_command | 4 | 31746 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU124_Mode_status | 246 | IU124_Mode_status | 13 | 31747 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU124_Mode_command | 246 | IU124_Mode_command | 14 | 31748 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU124_SetPoint_status | 246 | IU124_SetPoint_status | 0 | 31749 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU124_SetPoint_command | 246 | IU124_SetPoint_command | 1 | 31750 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU124_Room_Temperature | 246 | IU124_Room_Temperature | 0 | 31751 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU124_FanSpeed_status | 246 | IU124_FanSpeed_status | 13 | 31752 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU124_FanSpeed_command | 246 | IU124_FanSpeed_command | 14 | 31753 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU124_AirDirection_status | 246 | IU124_AirDirection_status | 13 | 31754 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU124_AirDirection_command | 246 | IU124_AirDirection_command | 14 | 31755 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU124_FilterSign_status | 246 | IU124_FilterSign_status | 3 | 31756 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU124_FilterSign_Reset_command | 246 | IU124_FilterSign_Reset_command | 4 | 31757 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU124_ErrorCode | 246 | IU124_ErrorCode | 13/0** | 31758 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU124_RemoteControl_Lock | 246 | IU124_RemoteControl_Lock | 19 | 31759 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU124_Occupancy | 246 | IU124_Occupancy | 19 | 31774 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU124_Consumption_Yesterday | 246 | IU124_Consumption_Yesterday | 0 | 31775 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU124_Consumption_Today | 246 | IU124_Consumption_Today | 0 | 31776 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU124_Consumption_Total | 246 | IU124_Consumption_Total | 0 | 31777 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU125_IU_Exist | 246 | IU125_IU_Exist | 3 | 32000 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU125_OnOff_status | 246 | IU125_OnOff_status | 3 | 32001 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU125_OnOff_command | 246 | IU125_OnOff_command | 4 | 32002 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU125_Mode_status | 246 | IU125_Mode_status | 13 | 32003 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU125_Mode_command | 246 | IU125_Mode_command | 14 | 32004 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU125_SetPoint_status | 246 | IU125_SetPoint_status | 0 | 32005 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU125_SetPoint_command | 246 | IU125_SetPoint_command | 1 | 32006 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU125_Room_Temperature | 246 | IU125_Room_Temperature | 0 | 32007 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU125_FanSpeed_status | 246 | IU125_FanSpeed_status | 13 | 32008 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU125_FanSpeed_command | 246 | IU125_FanSpeed_command | 14 | 32009 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU125_AirDirection_status | 246 | IU125_AirDirection_status | 13 | 32010 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU125_AirDirection_command | 246 | IU125_AirDirection_command | 14 | 32011 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU125_FilterSign_status | 246 | IU125_FilterSign_status | 3 | 32012 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU125_FilterSign_Reset_command | 246 | IU125_FilterSign_Reset_command | 4 | 32013 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU125_ErrorCode | 246 | IU125_ErrorCode | 13/0** | 32014 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU125_RemoteControl_Lock | 246 | IU125_RemoteControl_Lock | 19 | 32015 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU125_Occupancy | 246 | IU125_Occupancy | 19 | 32030 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU125_Consumption_Yesterday | 246 | IU125_Consumption_Yesterday | 0 | 32031 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU125_Consumption_Today | 246 | IU125_Consumption_Today | 0 | 32032 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU125_Consumption_Total | 246 | IU125_Consumption_Total | 0 | 32033 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU126_IU_Exist | 246 | IU126_IU_Exist | 3 | 32256 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU126_OnOff_status | 246 | IU126_OnOff_status | 3 | 32257 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU126_OnOff_command | 246 | IU126_OnOff_command | 4 | 32258 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU126_Mode_status | 246 | IU126_Mode_status | 13 | 32259 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU126_Mode_command | 246 | IU126_Mode_command | 14 | 32260 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU126_SetPoint_status | 246 | IU126_SetPoint_status | 0 | 32261 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU126_SetPoint_command | 246 | IU126_SetPoint_command | 1 | 32262 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU126_Room_Temperature | 246 | IU126_Room_Temperature | 0 | 32263 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU126_FanSpeed_status | 246 | IU126_FanSpeed_status | 13 | 32264 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU126_FanSpeed_command | 246 | IU126_FanSpeed_command | 14 | 32265 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU126_AirDirection_status | 246 | IU126_AirDirection_status | 13 | 32266 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU126_AirDirection_command | 246 | IU126_AirDirection_command | 14 | 32267 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU126_FilterSign_status | 246 | IU126_FilterSign_status | 3 | 32268 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU126_FilterSign_Reset_command | 246 | IU126_FilterSign_Reset_command | 4 | 32269 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU126_ErrorCode | 246 | IU126_ErrorCode | 13/0** | 32270 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU126_RemoteControl_Lock | 246 | IU126_RemoteControl_Lock | 19 | 32271 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU126_Occupancy | 246 | IU126_Occupancy | 19 | 32286 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU126_Consumption_Yesterday | 246 | IU126_Consumption_Yesterday | 0 | 32287 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU126_Consumption_Today | 246 | IU126_Consumption_Today | 0 | 32288 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU126_Consumption_Total | 246 | IU126_Consumption_Total | 0 | 32289 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU127_IU_Exist | 246 | IU127_IU_Exist | 3 | 32512 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU127_OnOff_status | 246 | IU127_OnOff_status | 3 | 32513 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU127_OnOff_command | 246 | IU127_OnOff_command | 4 | 32514 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU127_Mode_status | 246 | IU127_Mode_status | 13 | 32515 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU127_Mode_command | 246 | IU127_Mode_command | 14 | 32516 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU127_SetPoint_status | 246 | IU127_SetPoint_status | 0 | 32517 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU127_SetPoint_command | 246 | IU127_SetPoint_command | 1 | 32518 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU127_Room_Temperature | 246 | IU127_Room_Temperature | 0 | 32519 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU127_FanSpeed_status | 246 | IU127_FanSpeed_status | 13 | 32520 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU127_FanSpeed_command | 246 | IU127_FanSpeed_command | 14 | 32521 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU127_AirDirection_status | 246 | IU127_AirDirection_status | 13 | 32522 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU127_AirDirection_command | 246 | IU127_AirDirection_command | 14 | 32523 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU127_FilterSign_status | 246 | IU127_FilterSign_status | 3 | 32524 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU127_FilterSign_Reset_command | 246 | IU127_FilterSign_Reset_command | 4 | 32525 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU127_ErrorCode | 246 | IU127_ErrorCode | 13/0** | 32526 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU127_RemoteControl_Lock | 246 | IU127_RemoteControl_Lock | 19 | 32527 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU127_Occupancy | 246 | IU127_Occupancy | 19 | 32542 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU127_Consumption_Yesterday | 246 | IU127_Consumption_Yesterday | 0 | 32543 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU127_Consumption_Today | 246 | IU127_Consumption_Today | 0 | 32544 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU127_Consumption_Total | 246 | IU127_Consumption_Total | 0 | 32545 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19
IU128_IU_Exist | 246 | IU128_IU_Exist | 3 | 32768 | 2-OA-IA_IU_Exist |  |  |  | N | Y |  |  | 1
IU128_OnOff_status | 246 | IU128_OnOff_status | 3 | 32769 | 2-OA-IA_OnOff_status |  |  |  | N | Y |  |  | 1
IU128_OnOff_command | 246 | IU128_OnOff_command | 4 | 32770 | 2-OA-IA_OnOff_command |  |  |  | Y | Y |  |  | 1
IU128_Mode_status | 246 | IU128_Mode_status | 13 | 32771 | 2-OA-IA_Mode_status |  |  |  | N | Y |  |  | 2
IU128_Mode_command | 246 | IU128_Mode_command | 14 | 32772 | 2-OA-IA_Mode_command |  |  |  | Y | Y |  |  | 3
IU128_SetPoint_status | 246 | IU128_SetPoint_status | 0 | 32773 | 2-OA-IA_SetPoint_status |  | -15/5* | 60/140* | N | Y |  |  |  | 62/64*
IU128_SetPoint_command | 246 | IU128_SetPoint_command | 1 | 32774 | 2-OA-IA_SetPoint_command |  | -15/5* | 60/140* | Y | Y |  |  |  | 62/64*
IU128_Room_Temperature | 246 | IU128_Room_Temperature | 0 | 32775 | 2-OA-IA_Room_Temperature |  | -35/-31* | 92,5/140* | N | Y |  |  |  | 62/64*
IU128_FanSpeed_status | 246 | IU128_FanSpeed_status | 13 | 32776 | 2-OA-IA_FanSpeed_status |  |  |  | N | Y |  |  | 4
IU128_FanSpeed_command | 246 | IU128_FanSpeed_command | 14 | 32777 | 2-OA-IA_FanSpeed_command |  |  |  | Y | Y |  |  | 4
IU128_AirDirection_status | 246 | IU128_AirDirection_status | 13 | 32778 | 2-OA-IA_AirDirection_status |  |  |  | N | Y |  |  | 5
IU128_AirDirection_command | 246 | IU128_AirDirection_command | 14 | 32779 | 2-OA-IA_AirDirection_command |  |  |  | Y | Y |  |  | 5
IU128_FilterSign_status | 246 | IU128_FilterSign_status | 3 | 32780 | 2-OA-IA_FilterSign_status |  |  |  | N | Y |  |  | 1
IU128_FilterSign_Reset_command | 246 | IU128_FilterSign_Reset_command | 4 | 32781 | 2-OA-IA_FilterSign_Reset_command |  |  |  | Y | Y |  |  | 1
IU128_ErrorCode | 246 | IU128_ErrorCode | 13/0** | 32782 | 2-OA-IA_ErrorCode |  |  |  | N | Y |  |  | 0
IU128_RemoteControl_Lock | 246 | IU128_RemoteControl_Lock | 19 | 32783 | 2-OA-IA_RemoteControl_Lock |  |  |  | Y | Y |  |  | 6
IU128_Occupancy | 246 | IU128_Occupancy | 19 | 32798 | 2-OA-IA_Occupancy |  |  |  | Y | Y |  |  | 7
IU128_Consumption_Yesterday | 246 | IU128_Consumption_Yesterday | 0 | 32799 | 2-OA-IA_Consumption_Yesterday |  | 0 | 3E38 | N | Y |  |  |  | 19
IU128_Consumption_Today | 246 | IU128_Consumption_Today | 0 | 32800 | 2-OA-IA_Consumption_Today |  | 0 | 3E38 | N | Y |  |  |  | 19
IU128_Consumption_Total | 246 | IU128_Consumption_Total | 0 | 32801 | 2-OA-IA_Consumption_Total |  | 0 | 3E38 | N | Y |  |  |  | 19

## State-Texts
#State Text Reference
#Reference Number | Text 1 or Inactive-Text | Text 2 or Active-Text | Text 3 | Text 4 | Text 5 | Text 6 | Text 7 | Text 8 | Text 9 | Text 10 | Text 11 | Text 12 | Text 13 | Text 14 | Text 15 | Text 16 | Text 17 | Text 18 | Text 19 | Text 20 | Text 21 | Text 22 | Text 23 | Text 24 | Text 25 | Text 26 | Text 27 | Text 28 | Text 29 | Text 30 | Text 31 | Text 32 | Text 33 | Text 34 | Text 35 | Text 36 | Text 37 | Text 38 | Text 39 | Text 40 | Text 41 | Text 42 | Text 43 | Text 44 | Text 45 | Text 46 | Text 47 | Text 48 | Text 49 | Text 50 | Text 51 | Text 52 | Text 53 | Text 54 | Text 55 | Text 56 | Text 57 | Text 58 | Text 59 | Text 60 | Text 61 | Text 62 | Text 63 | Text 64 | Text 65 | Text 66 | Text 67 | Text 68 | Text 69 | Text 70 | Text 71 | Text 72 | Text 73 | Text 74 | Text 75 | Text 76 | Text 77 | Text 78 | Text 79 | Text 80 | Text 81 | Text 82 | Text 83 | Text 84 | Text 85 | Text 86 | Text 87 | Text 88 | Text 89 | Text 90 | Text 91 | Text 92 | Text 93 | Text 94 | Text 95 | Text 96 | Text 97 | Text 98 | Text 99 | Text 100 | Text 101 | Text 102 | Text 103 | Text 104 | Text 105 | Text 106 | Text 107 | Text 108 | Text 109 | Text 110 | Text 111 | Text 112 | Text 113 | Text 114 | Text 115 | Text 116 | Text 117 | Text 118 | Text 119 | Text 120 | Text 121 | Text 122 | Text 123 | Text 124 | Text 125 | Text 126 | Text 127 | Text 128 | Text 129 | Text 130 | Text 131 | Text 132 | Text 133 | Text 134 | Text 135 | Text 136 | Text 137 | Text 138 | Text 139 | Text 140 | Text 141 | Text 142 | Text 143 | Text 144 | Text 145 | Text 146 | Text 147 | Text 148 | Text 149 | Text 150 | Text 151 | Text 152 | Text 153 | Text 154 | Text 155 | Text 156 | Text 157 | Text 158 | Text 159 | Text 160 | Text 161 | Text 162 | Text 163 | Text 164 | Text 165 | Text 166 | Text 167 | Text 168 | Text 169 | Text 170 | Text 171 | Text 172 | Text 173 | Text 174 | Text 175 | Text 176 | Text 177 | Text 178 | Text 179 | Text 180 | Text 181 | Text 182 | Text 183 | Text 184 | Text 185 | Text 186 | Text 187 | Text 188 | Text 189 | Text 190 | Text 191 | Text 192 | Text 193 | Text 194 | Text 195 | Text 196 | Text 197 | Text 198 | Text 199 | Text 200 | Text 201 | Text 202 | Text 203 | Text 204 | Text 205 | Text 206 | Text 207 | Text 208 | Text 209 | Text 210 | Text 211 | Text 212 | Text 213 | Text 214 | Text 215 | Text 216 | Text 217 | Text 218 | Text 219 | Text 220 | Text 221 | Text 222 | Text 223 | Text 224 | Text 225 | Text 226 | Text 227 | Text 228 | Text 229 | Text 230 | Text 231 | Text 232 | Text 233 | Text 234 | Text 235 | Text 236 | Text 237 | Text 238 | Text 239 | Text 240 | Text 241 | Text 242 | Text 243 | Text 244 | Text 245 | Text 246 | Text 247 | Text 248 | Text 249 | Text 250 | Text 251 | Text 252 | Text 253 | Text 254 | Text 255 | Text 256 | Text 257 | Text 259 | Text 258
0 | A01 | A02 | A03 | A04 | A05 | A06 | A07 | A08 | A09 | A10 | A11 | A12 | A13 | A14 | A15 | A16 | A17 | A18 | A19 | A20 | A21 | A22 | A23 | A24 | A25 | A26 | A27 | A28 | A29 | A30 | A31 | ?? | C01 | C02 | C03 | C04 | C05 | C06 | C07 | C08 | C09 | C10 | C11 | C12 | C13 | C14 | C15 | C16 | C17 | C18 | C19 | C20 | C21 | C22 | C23 | C24 | C25 | C26 | C27 | C28 | C29 | C30 | C31 | ?? | E01 | E02 | E03 | E04 | E05 | E06 | E07 | E08 | E09 | E10 | E11 | E12 | E13 | E14 | E15 | E16 | E17 | E18 | E19 | E20 | E21 | E22 | E23 | E24 | E25 | E26 | E27 | E28 | E29 | E30 | E31 | ?? | F01 | F02 | F03 | F04 | F05 | F06 | F07 | F08 | F09 | F10 | F11 | F12 | F13 | F14 | F15 | F16 | F17 | F18 | F19 | F20 | F21 | F22 | F23 | F24 | F25 | F26 | F27 | F28 | F29 | F30 | F31 | ?? | H01 | H02 | H03 | H04 | H05 | H06 | H07 | H08 | H09 | H10 | H11 | H12 | H13 | H14 | H15 | H16 | H17 | H18 | H19 | H20 | H21 | H22 | H23 | H24 | H25 | H26 | H27 | H28 | H29 | H30 | H31 | ?? | J01 | J02 | J03 | J04 | J05 | J06 | J07 | J08 | J09 | J10 | J11 | J12 | J13 | J14 | J15 | J16 | J17 | J18 | J19 | J20 | J21 | J22 | J23 | J24 | J25 | J26 | J27 | J28 | J29 | J30 | J31 | ?? | L01 | L02 | L03 | L04 | L05 | L06 | L07 | L08 | L09 | L10 | L11 | L12 | L13 | L14 | L15 | L16 | L17 | L18 | L19 | L20 | L21 | L22 | L23 | L24 | L25 | L26 | L27 | L28 | L29 | L30 | L31 | ?? | P01 | P02 | P03 | P04 | P05 | P06 | P07 | P08 | P09 | P10 | P11 | P12 | P13 | P14 | P15 | P16 | P17 | P18 | P19 | P20 | P21 | P22 | P23 | P24 | P25 | P26 | P27 | P28 | P29 | P30 | P31 | Comm_Error | Not_Exist | Scan | Normal
1 | Inactive | Active
2 | Heat | Cool | Fan | Dry | AutoHeat | AutoCool
3 | Heat | Cool | Fan | Dry | Auto
4 | Low | Medium | High | Auto
5 | Horitzontal | Pos2 | Pos3 | Pos4 | Vertical | Swing | Off/Auto
6 | --/--/--/--/OO | --/--/--/OM/-- | --/--/--/OM/OO | --/--/SP/--/-- | --/--/SP/--/OO | --/--/SP/OM/-- | --/--/SP/OM/OO | --/AD/--/--/-- | --/AD/--/--/OO | --/AD/--/OM/-- | --/AD/--/OM/OO | --/AD/SP/--/-- | --/AD/SP/--/OO | --/AD/SP/OM/-- | --/AD/SP/OM/OO | FS/--/--/--/-- | FS/--/--/--/OO | FS/--/--/OM/-- | FS/--/--/OM/OO | FS/--/SP/--/-- | FS/--/SP/--/OO | FS/--/SP/OM/-- | FS/--/SP/OM/OO | FS/AD/--/--/-- | FS/AD/--/--/OO | FS/AD/--/OM/-- | FS/AD/--/OM/OO | FS/AD/SP/--/-- | FS/AD/SP/--/OO | FS/AD/SP/OM/-- | FS/AD/SP/OM/OO | --/--/--/--/--
7 | Occupied | Unoccupied | Disabled

## Unit-Texts
#Encoding of BACnet Engineering Units
#Code | Unit Text
62 | DEGREES-CELSIUS
64 | DEGREES-FAHRENHEIT
19 | KILOWATTS-HOUR

## Object-Types
#Encoding of BACnet Object Types
#Code | Object Type
0 | Analog Input
1 | Analog Output
2 | Analog Value
3 | Binary Input
4 | Binary Output
8 | Device
13 | Multistate Input
14 | Multistate Output
19 | Multistate Value